## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-01
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 25.4692 | 199.4663 | 35.8375
|  | #6-2 | Production | 22.9128 | 196.8442 | 34.3726
|  | #6-3 | Production | 21.2849 | 196.823 | 35.0505
|  | #6-4 | Production | 21.0381 | 197.4683 | 39.3839
|  | #8-1 | Shut in | 0.49087 | 79.5661 | 9.9742
|  | #8-2 | Production | 21.7555 | 191.042 | 48.2214
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 52.5901 | 4543787.6997
|  | PAD #8 - STEAM |  |  |  |  | 3.1217 | 269714.4172 | Online
|  | BRINE HEADER |  |  |  |  | 10.6195 | 917522.8334 | Offline
|  | TOTAL FLOW |  |  |  |  | 66.3313 | 5731024.9503
|  | PRESS SEPARATOR IJN 6 | Online | 13.1938 | 194.8092
|  | PRESS SEPARATOR IJN 8 | Online | 12.9811 | 194.2341
| INJECTION WELL | #5-1 | Injection | 15.8744 | 125.3173 | 99.9714 | 135.2931 | 11689324.5881
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.1948 |  |  | 820.676
|  | NET | 31.4606 |  |  | 755.0535
| PARASITIC LOAD |  | 2.7343 |  |  | 65.6225
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 1.9398 |  |  | 6983.2975
|  | NET | 2.1084 |  |  | 7590.2235
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Alarm at ABB Pluto Safety PLC cannot reset (K103 Contactor TCBR Fail, K105 Contactor VCBR Fail & K110 Contactor Emergency Stop Fail)
7. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 8. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
9. DHP tools pull out at Well IJN 9-1 and Well IJN8-1 was done by Toptek. Master valve and crown valve closed
10. Brine Dump Control valve Ijen-6 PV-2227A indication passing

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-01
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 755053.5195 |  | 0 |  | 755053.5195
|  |  |  | 755053.5195 |  | 0 |  | 755053.5195
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 755040 | [7 empty] | 755040
M-T-D GROSS GENERATION (kWHR) |  |  |  | 821485 | [7 empty] | 821485
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18354.54 | 0 | 5539.81 | 44.2 | 1628 | 1631 | 27197.55
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 18354.54 | -283254.3 | 5539.81 | 44.2 | 1628 | 1631 | 8843.01
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.1948 |  |  | 4.0799 |  | 19.5749
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 24
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 91.2%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 4543.7877 |  | 269.7144 |  |  | 5367.3576
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.05259 |  | 0.0031217 |  |  | 0.062122
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 917.5228
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.010619
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 6284.8804
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.072742
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 192.622 |  |  |  | 193.0012
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.5977 |  |  |  | 17.9621
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 18.5542 |  | 21.6603 |  |  | 19.5749
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Alarm at ABB Pluto Safety PLC cannot reset (K103 Contactor TCBR Fail, K105 Contactor VCBR Fail & K110 Contactor Emergency Stop Fail)
7. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
8. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
9. Brine Dump Control valve Ijen-6 PV-2227A indication passing
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
1:03 | Stop electrical pit pump IJN 6 (Level pond: 33.7%)
1:38 | Start pit pump IJN 8 (Level pond: 41%)
3:40 | Stop pit pump IJN 8 (Level pond: 37.4%)
3:41 | Start electrical pit pump IJN 6 (Level pond: 36.8%)
5:41 | Stop electrical pit pump IJN 6 (Level pond: 31.8%)
5:43 | Start pit pump IJN 8 (Level pond: 40.5%)
7:45 | Stop pit pump IJN 8 (Level pond: 36.9%)
8:30 | Daily Tool box meeting
9:30 | Start pit pump IJN-8 (Level pond: 40%)
9:51 | Calibrate flow meter panel injection IJN 5
10:38 | Stop pit pump IJN-8 (Level pond : 38.6%)
10:40 | Start electrical pit pump IJN 6 (Level pond: 39.8%)
10:58 | Adjust seal plan 53B booster pump B IJN-6
11:15 | Improvement of structure road to Pond IJN-6 area (Erosion issue)
13:25 | Inspection of switchgear (Standart activities schedule)
13:46 | Stop electrical pit pump IJN 6 (Level pond : 32.1%)
13:47 | Start pit pump IJN 8 (Level pond : 43.5%)
14:02 | LOTO breaker compressor B & LOTO line output air
14:05 | Replace air filter & cleaning surface inlet compressor B (MTC team)
14:15 | Drain brine manifold strainer (Standart activities schedule)
16:49 | Stop pit pump IJN 8 (Level pond : 37.8%)
16:50 | Start electrical pit pump IJN 6 (Level pond: 36.2%)
17:10 | Drain Suction Strainer Booster Pump (A) IJN 8 (Standart activities schedule)
19:51 | Stop pit pump IJN 6 (28.2%)
19:52 | Start pit pump IJN 8 (42%)
20:00 | Handover day shift to night shift
20:09 | Jockey pump run alarm
21:15 | Power Block monitoring
22:02 | Stop pit pump IJN 8 (Level pond: 37.9%)
22:03 | Start electrical pit pump IJN 6 (Level pond: 31.2%)
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Zakariya |  |  |  | CCR Operator : Ois |  |  |  | Steamfield : Dadan
Night Shift | Shift Leader : Hary |  |  |  | CCR Operator : Fauzan |  |  |  | Steamfield : Vandy
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-01
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2127850 | 2154910 | 27060 | 27060
(BACKUP) |  | 2126290 | 2126290 | 2153330 | 27040 | 27040
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 93101910 | 93856950 | 755040 | 755040
(BACKUP) |  | 93082960 | 93082960 | 93837780 | 754820 | 754820
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4142230 | 4158580 | 16350 | 16350
(BACKUP) |  | 4144060 | 4144060 | 4160410 | 16350 | 16350
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 101323255 | 102144740 | 821485 | 821485
TOTAL |  |  |  |  | 821485 | 821485
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 16530255 | 16628942 | 98687 | 98687
TOTAL |  |  |  |  | 98687 | 98687
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3089318.34 | 3107672.88 | 18354.54 | 18354.54
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 989758.41 | 995298.22 | 5539.81 | 5539.81
U Ijen 5 |  | 7258.6 | 7258.6 | 7302.8 | 44.2 | 44.2
U Ijen 6 |  | 247889 | 247889 | 249517 | 1628 | 1628
U Ijen 8 |  | 299837 | 299837 | 301468 | 1631 | 1631
TOTAL |  |  |  |  | 27197.55 | 27197.55
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-01 01:00 | 33.8936 | 5.0871 | 0.88423 | 0.92812 | 19.3281 | 2.1752 | 12.5952 | 192.6202 | 17.9454 | 193.041 | 25.3112 | 36.8654 | 14.3848 | 199.3554 | 22.3835 | 34.9741 | 14.0015 | 196.6712 | 21.0928 | 35.0565 | 14.1469 | 196.5838 | 20.7596 | 39.2493 | 14.1225 | 197.3409 | 194.7684 | 13.1771 | 52.0797 | 0.41403 | 9.9749 | 0 | 79.8161 | 21.7572 | 50.2709 | 13.3542 | 190.9293 | 194.2276 | 12.9779 | 3.1083 | 62.0813 | 11.6449 | 73.7262 | 15.8643 | 135.471 | 125.426 | 99.9648 | 15.8359 | 17.9454 | 193.041 | 122.8551 | 14.9486 | 33.4537 | 0.5454 | 78.3562 | 5.9767 | 0.13075 | 21.2031 | 0.16875 | 0.94433 | 0.45354
2025-06-01 02:00 | 33.9425 | 3.1589 | 0.88718 | 0.92757 | 19.1491 | 2.1706 | 12.5974 | 192.6205 | 17.9514 | 193.0108 | 25.3212 | 36.7495 | 14.3988 | 199.3975 | 22.3324 | 34.974 | 14.0105 | 196.7408 | 21.1862 | 35.0569 | 14.1655 | 196.698 | 20.8693 | 39.8735 | 14.1464 | 197.3082 | 194.775 | 13.1814 | 52.1099 | 0.48102 | 9.9765 | 0 | 79.6877 | 21.7533 | 50.263 | 13.3585 | 190.9331 | 194.2368 | 12.981 | 3.0982 | 62.2175 | 11.4582 | 73.6757 | 15.8714 | 135.1755 | 125.4004 | 99.9639 | 15.843 | 17.9514 | 193.0108 | 122.8333 | 14.9513 | 33.4139 | 0.45983 | 78.4421 | 7.2782 | 0.13071 | 21.3198 | 0.085337 | 0.86735 | 0.37405
2025-06-01 03:00 | 34.1953 | 0.50519 | 0.89233 | 0.92911 | 19.1072 | 2.1605 | 12.5977 | 192.6209 | 17.9641 | 192.9809 | 25.3401 | 36.2413 | 14.4179 | 199.4596 | 22.3991 | 34.9726 | 14.0295 | 196.7924 | 21.4309 | 35.0584 | 14.1921 | 196.8242 | 20.9488 | 40.2433 | 14.1759 | 197.446 | 194.8089 | 13.1914 | 52.5512 | 0.53448 | 9.9717 | 0 | 79.5628 | 21.7492 | 50.2402 | 13.3603 | 190.9387 | 194.2459 | 12.9835 | 3.0836 | 62.7184 | 11.1599 | 73.8783 | 15.8849 | 135.1086 | 125.4111 | 99.9634 | 15.8564 | 17.9641 | 192.9809 | 122.6645 | 14.9641 | 33.4431 | 0.45859 | 78.1922 | 7.3896 | 0.13408 | 21.8235 | 0.085227 | 0.86595 | 0.37323
2025-06-01 04:00 | 34.2605 | 0.24215 | 0.89189 | 0.92504 | 18.9442 | 2.1527 | 12.5922 | 192.6045 | 17.9599 | 192.9651 | 25.348 | 36.02 | 14.406 | 199.4362 | 22.4522 | 34.9702 | 14.0201 | 196.7304 | 21.419 | 35.0586 | 14.1781 | 196.7549 | 20.9011 | 39.9309 | 14.1587 | 197.4329 | 194.7945 | 13.1856 | 52.6399 | 0.55257 | 9.9654 | 0 | 79.4304 | 21.7443 | 50.2262 | 13.3524 | 190.9238 | 194.2296 | 12.9783 | 3.0756 | 62.7587 | 10.993 | 73.7517 | 15.8828 | 135.095 | 125.256 | 99.964 | 15.8544 | 17.9599 | 192.9651 | 122.4477 | 14.96 | 33.4189 | 0.45775 | 77.9962 | 6.5774 | 0.13792 | 22.1371 | 0.085001 | 0.86827 | 0.3727
2025-06-01 05:00 | 34.1621 | 0.59968 | 0.89832 | 0.92878 | 18.708 | 2.1502 | 12.5945 | 192.6113 | 17.9597 | 192.9644 | 25.3617 | 36.021 | 14.4048 | 199.439 | 22.4144 | 34.9693 | 14.0195 | 196.7251 | 21.1523 | 35.0578 | 14.1695 | 196.6826 | 20.9224 | 40.0501 | 14.1564 | 197.3758 | 194.7979 | 13.1861 | 52.4511 | 0.5286 | 9.9652 | 0 | 79.2899 | 21.742 | 50.2387 | 13.354 | 190.9227 | 194.2382 | 12.9802 | 3.0946 | 62.6375 | 10.8166 | 73.4541 | 15.8802 | 135.0573 | 125.1961 | 99.964 | 15.8516 | 17.9597 | 192.9644 | 122.5843 | 14.9598 | 33.4898 | 0.45831 | 78.0851 | 6.783 | 0.13721 | 21.9826 | 0.084987 | 0.86832 | 0.3729
2025-06-01 06:00 | 34.0278 | 0.79079 | 0.90153 | 0.9366 | 18.8038 | 2.1584 | 12.594 | 192.6099 | 17.954 | 192.9453 | 25.3637 | 36.0182 | 14.4031 | 199.4373 | 22.5335 | 34.9708 | 14.0224 | 196.7572 | 21.0847 | 35.0597 | 14.1624 | 196.7285 | 20.9457 | 40.0516 | 14.1595 | 197.3792 | 194.7843 | 13.1822 | 52.2965 | 0.50939 | 9.9696 | 0 | 79.1593 | 21.7432 | 50.2447 | 13.3551 | 190.9222 | 194.2307 | 12.979 | 3.1078 | 62.3891 | 11.0553 | 73.4444 | 15.8814 | 134.8854 | 125.3762 | 99.964 | 15.8529 | 17.954 | 192.9453 | 122.6623 | 14.954 | 33.3935 | 0.4639 | 78.1719 | 7.3749 | 0.13175 | 21.5541 | 0.085747 | 0.86194 | 0.37616
2025-06-01 07:00 | 34.265 | 1.6492 | 0.88514 | 0.92786 | 19.0795 | 2.1323 | 12.5939 | 192.6135 | 17.9612 | 192.9515 | 25.3761 | 36.0187 | 14.4237 | 199.4844 | 22.745 | 34.9929 | 14.0416 | 196.8316 | 21.3545 | 35.0606 | 14.1716 | 196.8885 | 20.9332 | 40.0548 | 14.1799 | 197.4412 | 194.804 | 13.1896 | 52.6458 | 0.52666 | 9.9757 | 0 | 79.1142 | 21.7562 | 50.228 | 13.3624 | 190.9668 | 194.2304 | 12.9799 | 3.1267 | 62.4627 | 10.6009 | 73.0636 | 15.8924 | 135.0857 | 125.4313 | 99.9674 | 15.8649 | 17.9612 | 192.9515 | 122.5159 | 14.9611 | 33.324 | 0.46271 | 78.161 | 7.7206 | 0.12109 | 22.2375 | 0.087804 | 0.83798 | 0.37392
2025-06-01 08:00 | 34.4233 | 2.64 | 0.88878 | 0.94037 | 19.9377 | 2.1048 | 12.6034 | 192.6506 | 17.9805 | 193.0078 | 25.4146 | 36.0227 | 14.4682 | 199.5575 | 22.7215 | 35.0268 | 14.0697 | 196.9181 | 21.5643 | 35.0569 | 14.1874 | 196.9963 | 20.9304 | 40.0636 | 14.2037 | 197.5451 | 194.8765 | 13.2125 | 53.0162 | 0.53845 | 9.9762 | 0 | 79.1527 | 21.7764 | 50.2041 | 13.3825 | 191.0334 | 194.269 | 12.99 | 3.1797 | 62.4323 | 10.0213 | 72.4537 | 15.9074 | 135.3845 | 125.1141 | 99.9721 | 15.8812 | 17.9805 | 193.0078 | 122.4781 | 14.9803 | 33.4867 | 0.4486 | 78.1036 | 6.9578 | 0.11258 | 22.9957 | 0.090045 | 0.79751 | 0.36483
2025-06-01 09:00 | 34.0319 | 2.9697 | 0.93283 | 0.98958 | 21.1328 | 2.1249 | 12.6029 | 192.6457 | 17.9742 | 193.0211 | 25.4461 | 36.03 | 14.4747 | 199.5301 | 22.6916 | 35.044 | 14.0681 | 196.9133 | 21.3232 | 35.0501 | 14.1756 | 196.8961 | 20.9454 | 40.0718 | 14.1945 | 197.5125 | 194.8692 | 13.2128 | 52.8823 | 0.53393 | 9.9747 | 0 | 79.2353 | 21.7927 | 50.1787 | 13.3882 | 191.0581 | 194.2612 | 12.9882 | 3.2095 | 62.1122 | 10.2021 | 72.3144 | 15.9073 | 135.2727 | 125.1574 | 99.9738 | 15.8825 | 17.9742 | 193.0211 | 122.9554 | 14.9741 | 33.4893 | 0.43353 | 78.7441 | 6.3034 | 0.11148 | 22.7832 | 0.091897 | 0.74308 | 0.35895
2025-06-01 10:00 | 33.7064 | 2.8907 | 0.95518 | 1.0135 | 21.6153 | 2.1448 | 12.5949 | 192.6118 | 17.9579 | 193.0008 | 25.4814 | 36.034 | 14.465 | 199.4735 | 22.7596 | 35.0456 | 14.0562 | 196.8692 | 21.0274 | 35.044 | 14.1601 | 196.8201 | 20.9577 | 40.076 | 14.1774 | 197.442 | 194.8111 | 13.1989 | 52.6149 | 0.54887 | 9.9776 | 0 | 79.3527 | 21.8 | 50.1829 | 13.3847 | 191.0808 | 194.2218 | 12.9784 | 3.1892 | 61.8828 | 10.4121 | 72.2949 | 15.9107 | 135.0277 | 125.8266 | 99.9754 | 15.8872 | 17.9579 | 193.0008 | 123.506 | 14.958 | 33.1951 | 0.40712 | 80.1019 | 6.7512 | 0.11216 | 22.3548 | 0.093261 | 0.68268 | 0.35252
2025-06-01 11:00 | 33.7581 | 2.6624 | 0.94738 | 1.0129 | 21.6603 | 2.1415 | 12.5959 | 192.6085 | 17.9616 | 193.0163 | 25.5001 | 36.3184 | 14.4936 | 199.5095 | 22.7485 | 35.0432 | 14.0742 | 196.9062 | 21.2317 | 35.0403 | 14.189 | 196.9483 | 20.9575 | 40.0788 | 14.1863 | 197.4974 | 194.8123 | 13.2012 | 52.6902 | 0.58956 | 9.9819 | 0 | 79.4742 | 21.7997 | 50.1843 | 13.389 | 191.1251 | 194.2193 | 12.9783 | 3.1796 | 62.0506 | 10.2441 | 72.2947 | 15.9283 | 135.0501 | 126.1832 | 99.9796 | 15.9061 | 17.9616 | 193.0163 | 123.4989 | 14.9617 | 33.0176 | 0.3891 | 80.7048 | 7.4493 | 0.11265 | 22.6837 | 0.093765 | 0.65703 | 0.34655
2025-06-01 12:00 | 34.3289 | 4.6305 | 0.92571 | 0.97951 | 21.2623 | 2.1117 | 12.6071 | 192.6439 | 17.992 | 193.0492 | 25.3708 | 37.3438 | 14.5438 | 199.6766 | 22.823 | 35.0433 | 14.1169 | 197.0584 | 21.6404 | 35.0386 | 14.2414 | 197.1509 | 20.9473 | 40.0802 | 14.227 | 197.6402 | 194.9011 | 13.2276 | 53.2404 | 0.61687 | 9.9832 | 0 | 79.5938 | 21.7948 | 50.1668 | 13.4014 | 191.2149 | 194.2646 | 12.9915 | 3.1941 | 62.7672 | 9.7237 | 72.4908 | 15.9549 | 135.4567 | 126.089 | 99.9831 | 15.9329 | 17.992 | 193.0492 | 123.1154 | 14.9918 | 33.1388 | 0.38504 | 79.9904 | 7.8092 | 0.11269 | 23.1278 | 0.093497 | 0.67929 | 0.3415
2025-06-01 13:00 | 34.8782 | 7.1603 | 0.89115 | 0.91814 | 20.3747 | 2.075 | 12.6198 | 192.6867 | 18.0144 | 193.1029 | 25.3299 | 37.5169 | 14.5706 | 199.7394 | 23.0385 | 35.0435 | 14.137 | 197.1393 | 21.5365 | 35.0378 | 14.2527 | 197.135 | 20.9843 | 39.7061 | 14.2402 | 197.7318 | 194.9674 | 13.2491 | 53.5387 | 0.57733 | 9.9837 | 0 | 79.7514 | 21.7961 | 49.8065 | 13.4155 | 191.2841 | 194.3108 | 13.0048 | 3.1944 | 63.1819 | 9.1898 | 72.3717 | 15.9662 | 135.9601 | 125.7537 | 99.9865 | 15.944 | 18.0144 | 193.1029 | 122.6153 | 15.0142 | 33.3989 | 0.38211 | 78.7555 | 6.1632 | 0.11267 | 22.9582 | 0.092725 | 0.71083 | 0.33618
2025-06-01 14:00 | 34.6002 | 7.201 | 0.8607 | 0.87691 | 19.7916 | 2.0855 | 12.6085 | 192.6501 | 17.9721 | 193.057 | 25.4826 | 36.0086 | 14.4969 | 199.4911 | 23.0594 | 35.0435 | 14.0735 | 196.91 | 21.0655 | 35.0386 | 14.1836 | 196.8445 | 20.9787 | 38.6979 | 14.1654 | 197.6043 | 194.8494 | 13.2136 | 52.7445 | 0.50157 | 9.9827 | 0 | 79.8783 | 21.7946 | 48.2857 | 13.3982 | 191.245 | 194.2547 | 12.989 | 3.1212 | 62.1352 | 10.0231 | 72.1583 | 15.9206 | 136.1128 | 125.1241 | 99.9886 | 15.8981 | 17.9721 | 193.057 | 122.3926 | 14.9722 | 33.488 | 0.40167 | 78.0579 | 4.6754 | 0.11239 | 22.0248 | 0.091641 | 0.73865 | 0.33436
2025-06-01 15:00 | 34.2805 | 5.8825 | 0.83812 | 0.85608 | 19.6193 | 2.114 | 12.5936 | 192.6011 | 17.9284 | 192.9998 | 25.5822 | 35.0688 | 14.4312 | 199.3217 | 22.9651 | 35.0418 | 14.0215 | 196.7415 | 21.0778 | 35.0425 | 14.1448 | 196.7613 | 21.01 | 38.0616 | 14.1151 | 197.4387 | 194.7296 | 13.1757 | 51.9795 | 0.48896 | 9.9799 | 0 | 79.9418 | 21.7808 | 47.1157 | 13.3727 | 191.1856 | 194.1908 | 12.9711 | 3.0671 | 61.0563 | 11.4117 | 72.468 | 15.88 | 135.9812 | 124.9138 | 99.9866 | 15.8567 | 17.9284 | 192.9998 | 122.3598 | 14.9284 | 33.4307 | 0.4188 | 77.8526 | 5.9927 | 0.11136 | 21.0179 | 0.090413 | 0.7646 | 0.33443
2025-06-01 16:00 | 34.4687 | 5.0103 | 0.83232 | 0.85043 | 19.2814 | 2.1023 | 12.5952 | 192.6069 | 17.9407 | 193.0361 | 25.5977 | 35.0773 | 14.4422 | 199.3922 | 22.9504 | 34.8936 | 14.0394 | 196.8194 | 21.5625 | 35.0467 | 14.1833 | 196.9252 | 21.1712 | 38.053 | 14.141 | 197.4808 | 194.7583 | 13.1834 | 52.2536 | 0.47502 | 9.9751 | 0 | 79.9816 | 21.7623 | 46.9884 | 13.3667 | 191.1682 | 194.2022 | 12.9746 | 3.0868 | 61.2804 | 11.1833 | 72.4636 | 15.8866 | 135.9844 | 124.9551 | 99.9827 | 15.8621 | 17.9407 | 193.0361 | 122.0204 | 14.9407 | 33.4858 | 0.42207 | 77.2179 | 7.0858 | 0.11052 | 21.4022 | 0.088838 | 0.78928 | 0.33574
2025-06-01 17:00 | 34.4492 | 6.1566 | 0.87298 | 0.89629 | 19.2422 | 2.0893 | 12.5937 | 192.6068 | 17.9621 | 193.0162 | 25.5801 | 35.0861 | 14.4356 | 199.454 | 22.9217 | 33.8767 | 14.0504 | 196.915 | 21.6578 | 35.0491 | 14.1968 | 196.9049 | 21.2514 | 38.0489 | 14.1555 | 197.5394 | 194.801 | 13.1924 | 52.8962 | 0.41842 | 9.9715 | 0 | 79.9512 | 21.7423 | 46.0282 | 13.3562 | 191.1151 | 194.213 | 12.977 | 3.1101 | 61.8307 | 10.1445 | 71.9751 | 15.8929 | 135.9358 | 124.6476 | 99.977 | 15.8665 | 17.9621 | 193.0162 | 122.146 | 14.962 | 33.6389 | 0.42995 | 77.1246 | 6.0475 | 0.11416 | 22.4139 | 0.087128 | 0.81612 | 0.33827
2025-06-01 18:00 | 34.3156 | 6.852 | 0.88439 | 0.90444 | 18.9713 | 2.1101 | 12.5945 | 192.612 | 17.9574 | 193.0065 | 25.566 | 35.0906 | 14.4064 | 199.4217 | 22.8795 | 33.0029 | 14.0284 | 196.931 | 21.1354 | 35.0497 | 14.168 | 196.6995 | 21.2575 | 38.06 | 14.1364 | 197.4658 | 194.7943 | 13.1863 | 52.6908 | 0.38943 | 9.9707 | 0 | 79.8782 | 21.7276 | 45.2003 | 13.3475 | 191.0616 | 194.2199 | 12.9771 | 3.1043 | 61.7407 | 10.6689 | 72.4096 | 15.8929 | 135.5751 | 125.0184 | 99.9711 | 15.8655 | 17.9574 | 193.0065 | 122.4265 | 14.9574 | 33.49 | 0.42836 | 77.6872 | 5.3184 | 0.12286 | 22.111 | 0.086049 | 0.8272 | 0.33879
2025-06-01 19:00 | 34.1255 | 5.8386 | 0.86491 | 0.88199 | 18.6536 | 2.1353 | 12.5949 | 192.6154 | 17.9407 | 193.0106 | 25.5586 | 35.0929 | 14.378 | 199.3638 | 23.1131 | 33.0005 | 13.9959 | 196.8399 | 20.9067 | 35.0501 | 14.1429 | 196.6516 | 21.2683 | 38.0682 | 14.1157 | 197.3936 | 194.7528 | 13.1728 | 52.0594 | 0.38908 | 9.9681 | 0 | 79.7869 | 21.7192 | 45.2102 | 13.343 | 191.0313 | 194.2155 | 12.9749 | 3.086 | 61.1887 | 11.6809 | 72.8697 | 15.8859 | 135.1711 | 125.2628 | 99.967 | 15.8579 | 17.9407 | 193.0106 | 122.3741 | 14.9407 | 33.2464 | 0.42761 | 77.8233 | 6.0883 | 0.13088 | 21.2607 | 0.085361 | 0.82834 | 0.33791
2025-06-01 20:00 | 34.0798 | 5.2678 | 0.85163 | 0.89634 | 18.5542 | 2.1263 | 12.5908 | 192.6048 | 17.9416 | 192.9974 | 25.5643 | 35.094 | 14.3765 | 199.3688 | 23.4028 | 33.0019 | 13.9912 | 196.7807 | 21.3607 | 35.0511 | 14.1555 | 196.7764 | 21.2791 | 38.0675 | 14.1206 | 197.4244 | 194.7385 | 13.1689 | 52.1192 | 0.40336 | 9.9661 | 0 | 79.6942 | 21.7171 | 45.2118 | 13.3391 | 190.9954 | 194.2028 | 12.9716 | 3.0682 | 61.0248 | 11.4402 | 72.4649 | 15.8875 | 134.9644 | 125.0993 | 99.9653 | 15.8591 | 17.9416 | 192.9974 | 122.1718 | 14.9414 | 33.2412 | 0.43048 | 77.6017 | 6.6275 | 0.13522 | 21.3563 | 0.085089 | 0.83016 | 0.33668
2025-06-01 21:00 | 34.2745 | 5.1721 | 0.86903 | 0.92275 | 18.8259 | 2.1003 | 12.5952 | 192.6219 | 17.9687 | 192.9778 | 25.5769 | 35.0954 | 14.4051 | 199.4573 | 23.3663 | 33.0031 | 14.0161 | 196.84 | 21.7125 | 35.0522 | 14.1878 | 196.8575 | 21.2456 | 38.7603 | 14.1542 | 197.4598 | 194.8064 | 13.1885 | 52.6534 | 0.42251 | 9.9681 | 0 | 79.6027 | 21.7181 | 45.2113 | 13.3477 | 190.9887 | 194.2322 | 12.9797 | 3.0916 | 61.7046 | 10.2828 | 71.9874 | 15.906 | 134.9523 | 124.9171 | 99.9642 | 15.8777 | 17.9687 | 192.9778 | 122.1254 | 14.9685 | 33.3759 | 0.43287 | 77.3602 | 6.0259 | 0.13546 | 22.43 | 0.085157 | 0.82925 | 0.33742
2025-06-01 22:00 | 34.2109 | 5.1882 | 0.91434 | 0.95524 | 19.5896 | 2.1136 | 12.5997 | 192.6373 | 17.9847 | 192.9516 | 25.5855 | 35.0958 | 14.4212 | 199.5021 | 23.2816 | 33.0029 | 14.0257 | 196.8776 | 21.3021 | 35.0523 | 14.1869 | 196.7414 | 21.2818 | 39.7562 | 14.1739 | 197.4407 | 194.8561 | 13.2027 | 52.9356 | 0.43203 | 9.9712 | 0 | 79.5097 | 21.721 | 45.2103 | 13.357 | 190.9796 | 194.2563 | 12.9861 | 3.1272 | 62.5708 | 9.7385 | 72.3093 | 15.9173 | 134.9293 | 124.9248 | 99.9629 | 15.8893 | 17.9847 | 192.9516 | 122.5102 | 14.9847 | 33.4384 | 0.43303 | 77.6367 | 5.1035 | 0.13234 | 22.8975 | 0.085415 | 0.82278 | 0.34121
2025-06-01 23:00 | 34.1248 | 5.0715 | 0.90133 | 0.94705 | 19.4414 | 2.1358 | 12.5953 | 192.6215 | 17.9675 | 192.9263 | 25.5963 | 35.095 | 14.4053 | 199.4396 | 23.241 | 33.0026 | 14.0041 | 196.8116 | 20.8681 | 35.0518 | 14.1589 | 196.6205 | 21.2109 | 40.0576 | 14.1548 | 197.432 | 194.8152 | 13.1895 | 52.6034 | 0.44799 | 9.9734 | 0 | 79.4225 | 21.7235 | 45.2132 | 13.3531 | 190.965 | 194.2342 | 12.9794 | 3.1225 | 62.5468 | 10.3369 | 72.8837 | 15.9136 | 134.7066 | 125.3896 | 99.9634 | 15.8858 | 17.9675 | 192.9263 | 122.5894 | 14.9675 | 33.2653 | 0.42426 | 78.0291 | 5.314 | 0.12932 | 22.27 | 0.085703 | 0.81571 | 0.34242
2025-06-02 | 33.8728 | 5.2915 | 0.87145 | 0.91668 | 18.7252 | 2.1432 | 12.5934 | 192.6016 | 17.9511 | 192.9926 | 25.6047 | 35.0954 | 14.4247 | 199.4835 | 24.6846 | 33.0032 | 14.0466 | 196.7396 | 21.1452 | 35.0528 | 14.1944 | 196.8611 | 20.9567 | 40.0537 | 14.1765 | 197.4654 | 194.7494 | 13.1811 | 52.4707 | 0.46071 | 9.9778 | 0 | 79.3194 | 21.7205 | 45.203 | 13.3483 | 190.9405 | 194.2119 | 12.9763 | 3.0944 | 62.1614 | 10.4348 | 72.5962 | 15.9017 | 134.6913 | 125.7418 | 99.9629 | 15.8741 | 17.9511 | 192.9926 | 122.4367 | 14.9504 | 33.103 | 0.42147 | 77.7803 | 9.8817 | 0.13013 | 22.98 | 0.085454 | 0.82085 | 0.33822
Total | MW: 820.676; MVAR: 97.9187; kg/s: 4543787.6997; kg/s: 269714.4172; kg/s: 5367357.5853; kg/s: 917522.8334; kg/s: 6284880.4188; kg/s: 11689324.5881
Average | 34.1948 | 4.0799 | 0.88929 | 0.92756 | 19.5749 | 2.1274 | 12.5977 | 192.622 | 17.9621 | 193.0012 | 25.4692 | 35.8375 | 14.4366 | 199.4663 | 22.9128 | 34.3726 | 14.04 | 196.8442 | 21.2849 | 35.0505 | 14.179 | 196.823 | 21.0381 | 39.3839 | 14.1641 | 197.4683 | 194.8092 | 13.1938 | 52.5901 | 0.49087 | 9.9742 | 0 | 79.5661 | 21.7555 | 48.2214 | 13.3662 | 191.042 | 194.2341 | 12.9811 | 3.1217 | 62.1222 | 10.6195 | 72.7417 | 15.9007 | 135.2931 | 125.3173 | 99.9714 | 15.8744 | 17.9621 | 193.0012 | 122.5952 | 14.9622 | 33.3695 | 0.43427 | 78.249 | 6.6123 | 0.12343 | 22.1386 | 0.091429 | 0.80281 | 0.35469
Min | 33.7064 | 0.24215 | 0.83232 | 0.85043 | 18.5542 | 2.075 | 12.5908 | 192.6011 | 17.9284 | 192.9263 | 25.3112 | 35.0688 | 14.3765 | 199.3217 | 22.3324 | 33.0005 | 13.9912 | 196.6712 | 20.8681 | 35.0378 | 14.1429 | 196.5838 | 20.7596 | 38.0489 | 14.1151 | 197.3082 | 194.7296 | 13.1689 | 51.9795 | 0.38908 | 9.9652 | 0 | 79.1142 | 21.7171 | 45.2003 | 13.3391 | 190.9222 | 194.1908 | 12.9711 | 3.0671 | 61.0248 | 9.1898 | 71.9751 | 15.8643 | 134.6913 | 124.6476 | 99.9629 | 15.8359 | 17.9284 | 192.9263 | 122.0204 | 14.9284 | 33.0176 | 0.38211 | 77.1246 | 4.6754 | 0.11052 | 21.0179 | 0.084987 | 0.65703 | 0.33436
Max | 34.8782 | 7.201 | 0.95518 | 1.0135 | 21.6603 | 2.1752 | 12.6198 | 192.6867 | 18.0144 | 193.1029 | 25.6047 | 37.5169 | 14.5706 | 199.7394 | 24.6846 | 35.0456 | 14.137 | 197.1393 | 21.7125 | 35.0606 | 14.2527 | 197.1509 | 21.2818 | 40.2433 | 14.2402 | 197.7318 | 194.9674 | 13.2491 | 53.5387 | 0.61687 | 9.9837 | 0 | 79.9816 | 21.8 | 50.2709 | 13.4155 | 191.2841 | 194.3108 | 13.0048 | 3.2095 | 63.1819 | 11.6809 | 73.8783 | 15.9662 | 136.1128 | 126.1832 | 99.9886 | 15.944 | 18.0144 | 193.1029 | 123.506 | 15.0142 | 33.6389 | 0.5454 | 80.7048 | 9.8817 | 0.13792 | 23.1278 | 0.16875 | 0.94433 | 0.45354