## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-02
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 25.9255 | 199.6104 | 34.7951
|  | #6-2 | Production | 23.8345 | 197.0364 | 34.5204
|  | #6-3 | Production | 21.3339 | 197.1309 | 34.9179
|  | #6-4 | Production | 21.3123 | 197.5912 | 37.8156
|  | #8-1 | Shut in | 0.48049 | 79.6502 | 9.974
|  | #8-2 | Production | 22.2506 | 191.2884 | 42.9071
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 51.7918 | 4474815.3638
|  | PAD #8 - STEAM |  |  |  |  | 3.4653 | 299401.0551 | Online
|  | BRINE HEADER |  |  |  |  | 11.6452 | 1006146.2728 | Offline
|  | TOTAL FLOW |  |  |  |  | 66.9023 | 5780362.6916
|  | PRESS SEPARATOR IJN 6 | Online | 13.2772 | 195.0926
|  | PRESS SEPARATOR IJN 8 | Online | 13.0568 | 194.5172
| INJECTION WELL | #5-1 | Injection | 15.889 | 125.3566 | 99.9755 | 135.2065 | 11681843.4887
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 33.8835 |  |  | 813.204
|  | NET | 31.1673 |  |  | 748.015
| PARASITIC LOAD |  | 2.7162 |  |  | 65.189
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 1.9745 |  |  | 7108.1332
|  | NET | 2.1466 |  |  | 7727.6021
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Alarm at ABB Pluto Safety PLC cannot reset (K103 Contactor TCBR Fail, K105 Contactor VCBR Fail & K110 Contactor Emergency Stop Fail)
7. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 8. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
9. DHP tools pull out at Well IJN 9-1 and Well IJN8-1 was done by Toptek. Master valve and crown valve closed
10. Brine Dump Control valve Ijen-6 PV-2227A indication passing

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-02
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 748015.0479 |  | 0 |  | 748015.0479
|  |  |  | 748015.0479 |  | 0 |  | 748015.0479
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 746380 | [7 empty] | 746380
M-T-D GROSS GENERATION (kWHR) |  |  |  | 1633680 | [7 empty] | 1633680
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 17885.63 | 0 | 5466.06 | 44.1 | 1369 | 1747 | 26511.79
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 36240.17 | -283254.3 | 11005.87 | 88.3 | 2997 | 3378 | 17469.17
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 33.8835 |  |  | 5.4041 |  | 19.158
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 48
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 90.35%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 4474.8154 |  | 299.4011 |  |  | 5324.8119
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.051792 |  | 0.0034653 |  |  | 0.06163
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 1006.1463
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.011645
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 6330.9582
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.073275
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 192.9468 |  |  |  | 193.0905
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.6903 |  |  |  | 17.9573
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 17.684 |  | 20.6274 |  |  | 19.158
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Alarm at ABB Pluto Safety PLC cannot reset (K103 Contactor TCBR Fail, K105 Contactor VCBR Fail & K110 Contactor Emergency Stop Fail)
7. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
8. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
9. Brine Dump Control valve Ijen-6 PV-2227A indication passing
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:02 | Stop electrical pit pump IJN 6 (Level pond: 23.9%)
0:04 | Start pit pump IJN 8 (Level pond: 41% / 5 stages) (Discharge pressure: 21.5 barg)
2:05 | Stop pit pump IJN 8 (Level pond: 37.4%)
2:06 | Start electrical pit pump IJN 6 (Level pond: 26.7%)
4:07 | Stop electrical pit pump IJN 6 (Level pond: 19.1%)
4:08 | Start pit pump IJN 8 (Level pond: 40.6%)
6:09 | Stop pit pump IJN 8 (Level pond: 36.9%)
6:10 | Start electrical pit pump IJN 6 (Level pond: 22%)
8:15 | Daily tools box meeting
8:24 | Stop electrical pit pump IJN 6 (Level pond 18%)
8:25 | Start pit pump IJN 8 (Level pond 40.6%)
9:17 | Pull out jumper TCBR (Mr Tal mates ORMAT) & monitoring in HMI
9:35 | PLN dispatch (Mr Rendy N) advice load at 30.00 MW as grid requirment
9:50 | LOTO breaker & line outlet service water pump B
9:58 | Cleaning strainer Service water pump B & Rectify check valve (MTC team)
11:23 | Stop pit pump IJN 8 (Level 35.4%)
11:40 | Installation PLN radio telecomunication by Multifab
13:26 | P8051 Backwash Pump of well water treatment system run test (Standart activities schedule)
13:53 | PLN dispatch (Mr Tulus) advice load at 31.05 MW as grid requirment
13:49 | Drain air vessel IJN-8 (Standart activities schedule)
13:55 | Drain condensate pot at steam trap IJN-8 near powerblock (Standart activites schedule)
13:59 | Drain condensate pot at steam trap IJN-8 near separator (Standart activites schedule)
14:15 | Drain air vessel IJN-6 (Standart activities schedule)
14:38 | Drain condensate pot at steam trap IJN-6 near separator (Standart activites schedule)
14:45 | Drain condensate pot at steam trap IJN-6 near powerblock (Standart activites schedule)
17:25 | Drain Condensate pot steam trap steam gathering Near Condensate Pump (Standart activities schedule)
17:45 | Draining of Air Vessel Tank on Power Block (Standart activities schedule)
18:15 | Run test compressor standby (Standart activities schedule)
18:26 | Start pit pump IJN 8 (Level 33.8%)
19:45 | Handover day shift to night shift
20:50 | Stop pit pump IJN 8 (Level pond: 28.9%)
20:51 | Start electrical pit pump IJN 6 (Level pond: 35.1%)
21:15 | Power block monitoring
23:51 | Stop electrical pit pump IJN 6 (Level pond: 25%)
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Zakariya |  |  |  | CCR Operator : Ois |  |  |  | Steamfield : Dadan
Night Shift | Shift Leader : Hary |  |  |  | CCR Operator : Fauzan |  |  |  | Steamfield : Vandy
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-02
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2154910 | 2158700 | 3790 | 30850
(BACKUP) |  | 2126290 | 2153330 | 2157110 | 3780 | 30820
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 93856950 | 94603330 | 746380 | 1501420
(BACKUP) |  | 93082960 | 93837780 | 94583950 | 746170 | 1500990
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4158580 | 4183740 | 25160 | 41510
(BACKUP) |  | 4144060 | 4160410 | 4185590 | 25180 | 41530
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 102144740 | 102956935 | 812195 | 1633680
TOTAL |  |  |  |  | 812195 | 1633680
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 16628942 | 16759470 | 130528 | 229215
TOTAL |  |  |  |  | 130528 | 229215
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3107672.88 | 3125558.51 | 17885.63 | 36240.17
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 995298.22 | 1000764.28 | 5466.06 | 11005.87
U Ijen 5 |  | 7258.6 | 7302.8 | 7346.9 | 44.1 | 88.3
U Ijen 6 |  | 247889 | 249517 | 250886 | 1369 | 2997
U Ijen 8 |  | 299837 | 301468 | 303215 | 1747 | 3378
TOTAL |  |  |  |  | 26511.79 | 53709.34
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-02 01:00 | 34.373 | 4.1446 | 0.88392 | 0.91764 | 18.5018 | 2.1069 | 12.5989 | 192.6324 | 17.9806 | 192.9221 | 25.6092 | 35.0959 | 14.426 | 199.516 | 23.5558 | 33.0028 | 14.0341 | 196.8557 | 21.692 | 35.055 | 14.2081 | 196.8928 | 20.9348 | 40.0486 | 14.1756 | 197.4829 | 194.8385 | 13.1985 | 52.8624 | 0.39415 | 9.9706 | 0 | 79.1825 | 21.7171 | 45.2006 | 13.3527 | 190.953 | 194.2514 | 12.9846 | 3.1413 | 62.8963 | 9.5255 | 72.4218 | 15.9164 | 134.8105 | 125.003 | 99.9605 | 15.8883 | 17.9806 | 192.9221 | 122.2147 | 14.9805 | 33.4252 | 0.42166 | 77.2533 | 6.5785 | 0.1402 | 22.735 | 0.085149 | 0.82519 | 0.33596
2025-06-02 02:00 | 34.5666 | 3.9269 | 0.88886 | 0.90972 | 18.2705 | 2.093 | 12.5973 | 192.6277 | 17.9853 | 192.9251 | 25.6141 | 35.0966 | 14.4196 | 199.5113 | 23.504 | 33.0021 | 14.0274 | 196.8441 | 21.4738 | 35.055 | 14.1939 | 196.7521 | 20.9482 | 40.0501 | 14.1677 | 197.4642 | 194.8508 | 13.2008 | 53.0296 | 0.35571 | 9.9743 | 0 | 79.0477 | 21.7114 | 45.2111 | 13.3502 | 190.9473 | 194.2494 | 12.9842 | 3.1185 | 63.0895 | 9.2567 | 72.3463 | 15.9205 | 134.9387 | 124.9474 | 99.9604 | 15.8923 | 17.9853 | 192.9251 | 122.1914 | 14.9852 | 33.4693 | 0.42072 | 77.132 | 4.9734 | 0.14322 | 23.2487 | 0.084841 | 0.82969 | 0.33551
2025-06-02 03:00 | 34.3462 | 4.9589 | 0.87855 | 0.90302 | 18.499 | 2.1222 | 12.5914 | 192.6051 | 17.9606 | 192.9151 | 25.6283 | 35.0964 | 14.3924 | 199.4244 | 23.423 | 33.0026 | 13.996 | 196.7434 | 20.9287 | 35.0535 | 14.1529 | 196.5743 | 20.949 | 40.0535 | 14.1368 | 197.3656 | 194.7874 | 13.1814 | 52.5198 | 0.38904 | 9.9727 | 0 | 78.9335 | 21.7111 | 45.21 | 13.342 | 190.9272 | 194.2165 | 12.9751 | 3.0951 | 62.5314 | 10.3588 | 72.8902 | 15.9031 | 134.9228 | 124.9759 | 99.9613 | 15.8746 | 17.9606 | 192.9151 | 122.1287 | 14.9607 | 33.3337 | 0.42426 | 77.1421 | 5.1391 | 0.14117 | 22.2864 | 0.084804 | 0.83173 | 0.33632
2025-06-02 04:00 | 34.0706 | 5.8147 | 0.88684 | 0.92169 | 19.29 | 2.1336 | 12.591 | 192.6043 | 17.9564 | 192.9103 | 25.6247 | 35.0965 | 14.3933 | 199.429 | 23.5962 | 33.4839 | 13.9999 | 196.7558 | 21.0493 | 35.0529 | 14.1611 | 196.6945 | 20.9354 | 40.0538 | 14.1419 | 197.3762 | 194.7698 | 13.1771 | 52.3722 | 0.41422 | 9.9694 | 0 | 78.8306 | 21.7125 | 45.2057 | 13.3414 | 190.9152 | 194.2117 | 12.9739 | 3.1253 | 62.3379 | 10.3551 | 72.6929 | 15.8988 | 134.817 | 124.9912 | 99.9621 | 15.8702 | 17.9564 | 192.9103 | 122.3838 | 14.9565 | 33.3194 | 0.42827 | 77.5092 | 6.5783 | 0.14055 | 21.9588 | 0.084816 | 0.82996 | 0.33716
2025-06-02 05:00 | 34.367 | 5.3586 | 0.87933 | 0.92128 | 19.0403 | 2.1068 | 12.598 | 192.6299 | 17.9801 | 192.9279 | 25.6257 | 35.0973 | 14.4202 | 199.5175 | 23.7039 | 34.3639 | 14.032 | 196.8757 | 21.5945 | 35.053 | 14.202 | 196.8903 | 20.9172 | 40.0528 | 14.1735 | 197.4772 | 194.8319 | 13.1955 | 52.7991 | 0.39706 | 9.9707 | 0 | 78.7313 | 21.7084 | 45.2104 | 13.3484 | 190.946 | 194.2448 | 12.9834 | 3.1467 | 62.7475 | 9.6574 | 72.4049 | 15.9256 | 134.7851 | 125.1638 | 99.963 | 15.8974 | 17.9801 | 192.9279 | 122.2911 | 14.9802 | 33.3229 | 0.42575 | 77.4585 | 6.8763 | 0.14288 | 22.8153 | 0.084714 | 0.82986 | 0.33664
2025-06-02 06:00 | 34.5757 | 4.9469 | 0.88349 | 0.91681 | 18.7407 | 2.0926 | 12.5989 | 192.6362 | 17.9905 | 192.9235 | 25.6253 | 35.0963 | 14.4202 | 199.5393 | 23.5965 | 34.7664 | 14.0348 | 196.9163 | 21.5762 | 35.0556 | 14.1912 | 196.8178 | 20.9042 | 40.049 | 14.1769 | 197.4858 | 194.8653 | 13.2025 | 53.122 | 0.40271 | 9.9738 | 0 | 78.6673 | 21.7064 | 45.2074 | 13.3511 | 190.9878 | 194.2496 | 12.9859 | 3.1566 | 63.047 | 9.3062 | 72.3533 | 15.9333 | 135.0788 | 124.915 | 99.9656 | 15.9051 | 17.9905 | 192.9235 | 121.9315 | 14.9906 | 33.4005 | 0.4337 | 76.8649 | 5.4401 | 0.1389 | 23.1472 | 0.085638 | 0.82862 | 0.34386
2025-06-02 07:00 | 34.2036 | 4.3783 | 0.8991 | 0.93831 | 19.5139 | 2.1082 | 12.5931 | 192.6184 | 17.9655 | 192.9174 | 25.6238 | 35.0902 | 14.401 | 199.4621 | 23.6092 | 34.7811 | 14.0092 | 196.8433 | 21.0268 | 35.0583 | 14.1336 | 196.636 | 20.8977 | 40.055 | 14.1542 | 197.3748 | 194.8147 | 13.1879 | 52.7442 | 0.41689 | 9.9745 | 0 | 78.6933 | 21.7297 | 45.1831 | 13.3534 | 191.0065 | 194.216 | 12.9773 | 3.1548 | 62.2636 | 9.8459 | 72.1095 | 15.9105 | 135.2058 | 124.8667 | 99.9727 | 15.8838 | 17.9655 | 192.9174 | 122.2769 | 14.9657 | 33.4062 | 0.44076 | 77.294 | 5.2402 | 0.12303 | 22.5714 | 0.088342 | 0.80649 | 0.35151
2025-06-02 08:00 | 33.986 | 4.7255 | 0.89969 | 0.95128 | 20.3512 | 2.1125 | 12.594 | 192.6188 | 17.9551 | 192.9327 | 25.6441 | 35.0829 | 14.4244 | 199.4443 | 23.7434 | 34.7976 | 14.016 | 196.834 | 20.9646 | 35.0562 | 14.1266 | 196.7129 | 20.9037 | 40.067 | 14.1563 | 197.3547 | 194.7963 | 13.1862 | 52.4723 | 0.43293 | 9.9734 | 0 | 78.7967 | 21.758 | 45.1517 | 13.3662 | 191.0529 | 194.2127 | 12.976 | 3.1332 | 61.6247 | 10.1718 | 71.7965 | 15.9174 | 135.027 | 125.2934 | 99.9804 | 15.893 | 17.9551 | 192.9327 | 122.7889 | 14.9553 | 33.2325 | 0.4177 | 78.2849 | 6.4128 | 0.11207 | 22.405 | 0.091078 | 0.75946 | 0.34874
2025-06-02 09:00 | 34.101 | 6.2313 | 0.88608 | 0.92137 | 20.6274 | 2.1037 | 12.6278 | 192.7044 | 17.9738 | 192.9697 | 25.7644 | 34.4414 | 14.4487 | 199.4664 | 23.7981 | 34.8076 | 14.0542 | 196.9587 | 21.4841 | 35.0456 | 14.1691 | 196.9265 | 20.9793 | 39.4452 | 14.1856 | 197.474 | 194.8803 | 13.222 | 52.4191 | 0.47585 | 9.9754 | 0 | 79.015 | 21.7781 | 45.1353 | 13.4069 | 191.229 | 194.2894 | 13.0079 | 3.2517 | 61.452 | 10.2848 | 71.7368 | 15.9453 | 135.1513 | 125.4888 | 99.9874 | 15.9224 | 17.9738 | 192.9697 | 122.4961 | 14.9736 | 33.1525 | 0.3868 | 78.2486 | 6.2092 | 0.11384 | 21.5599 | 0.093532 | 0.71839 | 0.3492
2025-06-02 10:00 | 33.5844 | 6.3356 | 0.86329 | 0.88463 | 20.5586 | 2.1777 | 12.7184 | 193.0517 | 17.9616 | 193.086 | 26.0913 | 32.9749 | 14.4714 | 199.4886 | 23.7003 | 34.823 | 14.0991 | 197.1295 | 21.7018 | 35.0244 | 14.2126 | 197.0567 | 20.9413 | 37.447 | 14.2008 | 197.6496 | 195.1677 | 13.3021 | 51.3528 | 0.50901 | 9.9812 | 0 | 79.3524 | 21.9017 | 42.6252 | 13.4645 | 191.5246 | 194.5835 | 13.0779 | 3.465 | 60.8918 | 12.246 | 73.1378 | 15.9313 | 135.481 | 125.3431 | 99.9931 | 15.9098 | 17.9616 | 193.086 | 122.9952 | 14.9617 | 33.417 | 0.3581 | 78.7443 | 4.6737 | 0.11784 | 16.3004 | 0.095073 | 0.68839 | 0.4397
2025-06-02 11:00 | 32.7622 | 5.2582 | 0.84962 | 0.86837 | 20.4714 | 2.2781 | 12.6838 | 192.9439 | 17.8406 | 193.1303 | 26.377 | 32.1437 | 14.4029 | 199.1829 | 23.847 | 34.8346 | 14.029 | 196.8499 | 21.2349 | 35.0075 | 14.1374 | 196.7431 | 20.944 | 36.0909 | 14.0979 | 197.434 | 194.9813 | 13.2437 | 50.1194 | 0.50361 | 9.9874 | 0 | 79.6749 | 22.1683 | 42.5546 | 13.412 | 191.417 | 194.4323 | 13.0271 | 3.3413 | 60.3209 | 14.3147 | 74.6356 | 15.841 | 134.8477 | 125.8044 | 99.9937 | 15.8202 | 17.8406 | 193.1303 | 123.518 | 14.8408 | 33.0992 | 0.34406 | 79.8018 | 5.7085 | 0.11868 | 12.199 | 0.094829 | 0.67519 | 0.42494
2025-06-02 12:00 | 32.6466 | 4.4399 | 0.83343 | 0.85108 | 20.0801 | 2.2878 | 12.6455 | 192.766 | 17.7963 | 193.0221 | 26.4663 | 32.1407 | 14.3666 | 199.0356 | 23.9376 | 34.8372 | 13.987 | 196.6567 | 20.9915 | 35.0139 | 14.1016 | 196.6298 | 21.2679 | 36.1069 | 14.0562 | 197.3049 | 194.7736 | 13.1926 | 49.7153 | 0.49658 | 9.9868 | 0 | 79.8908 | 22.3578 | 44.9909 | 13.3832 | 191.2558 | 194.2708 | 12.9916 | 3.336 | 59.7674 | 14.9202 | 74.6876 | 15.811 | 134.4736 | 126.1008 | 99.9918 | 15.7895 | 17.7963 | 193.0221 | 123.2501 | 14.7962 | 32.8666 | 0.346 | 79.8243 | 7.9985 | 0.11669 | 12.1811 | 0.093549 | 0.69431 | 0.36664
2025-06-02 13:00 | 32.897 | 5.2778 | 0.82337 | 0.83988 | 19.6954 | 2.2774 | 12.7362 | 193.0964 | 17.8937 | 193.0482 | 26.4818 | 32.6196 | 14.4615 | 199.3735 | 23.856 | 34.8392 | 14.0847 | 196.9864 | 21.39 | 35.0282 | 14.2156 | 197.0655 | 21.5982 | 36.1049 | 14.1673 | 197.6649 | 195.1184 | 13.2932 | 49.9118 | 0.51852 | 9.9822 | 0 | 79.9987 | 22.4077 | 44.9993 | 13.4623 | 191.483 | 194.6446 | 13.0859 | 3.6727 | 60.2035 | 14.7165 | 74.92 | 15.8816 | 135.1032 | 125.9087 | 99.9894 | 15.8586 | 17.8937 | 193.0482 | 123.309 | 14.8936 | 33.3108 | 0.3575 | 79.3027 | 8.5978 | 0.11358 | 12.3629 | 0.091591 | 0.73493 | 0.6019
2025-06-02 14:00 | 33.3321 | 6.0083 | 0.82464 | 0.84009 | 19.4921 | 2.223 | 12.7306 | 193.086 | 17.9136 | 193.0509 | 26.3816 | 34.1224 | 14.4829 | 199.4973 | 23.7878 | 34.8393 | 14.1034 | 197.0814 | 21.6322 | 35.0337 | 14.2438 | 197.1635 | 21.704 | 36.2172 | 14.1961 | 197.7739 | 195.1611 | 13.3035 | 50.6527 | 0.52903 | 9.9771 | 0 | 80.0733 | 22.4376 | 45.0085 | 13.4546 | 191.5122 | 194.658 | 13.0864 | 3.5909 | 60.3894 | 13.708 | 74.0974 | 15.8956 | 135.2289 | 125.8506 | 99.9863 | 15.8719 | 17.9136 | 193.0509 | 122.8644 | 14.9134 | 33.331 | 0.37593 | 78.4219 | 8.6027 | 0.1112 | 13.3593 | 0.090127 | 0.768 | 0.63597
2025-06-02 15:00 | 33.8107 | 5.3892 | 0.8276 | 0.84343 | 19.3254 | 2.1745 | 12.7675 | 193.1778 | 17.9704 | 193.0107 | 26.2149 | 35.5834 | 14.5678 | 199.7593 | 23.9675 | 34.8379 | 14.1694 | 197.2475 | 21.2899 | 35.0353 | 14.3033 | 197.2466 | 21.7224 | 37.1909 | 14.269 | 197.8514 | 195.3019 | 13.3548 | 51.4351 | 0.50202 | 9.9722 | 0 | 80.1783 | 22.4633 | 44.7465 | 13.4889 | 191.573 | 194.748 | 13.1267 | 3.5972 | 60.7513 | 12.7709 | 73.5223 | 15.9278 | 135.7341 | 125.4042 | 99.9838 | 15.9035 | 17.9704 | 193.0107 | 122.6602 | 14.9704 | 33.6991 | 0.37944 | 77.6619 | 8.0883 | 0.11028 | 14.2047 | 0.089497 | 0.77903 | 0.75091
2025-06-02 16:00 | 33.9851 | 4.4048 | 0.80981 | 0.82553 | 18.9784 | 2.1913 | 12.8077 | 193.3496 | 18.01 | 193.2031 | 26.1181 | 36.0215 | 14.611 | 199.9424 | 24.0622 | 34.8369 | 14.2074 | 197.3921 | 20.9983 | 34.8215 | 14.3443 | 197.3954 | 21.6656 | 37.4327 | 14.3086 | 197.8989 | 195.475 | 13.3975 | 51.519 | 0.48683 | 9.971 | 0 | 80.2577 | 22.506 | 41.2454 | 13.5076 | 191.6694 | 194.9139 | 13.1633 | 3.5385 | 61.6682 | 12.8041 | 74.4723 | 15.9568 | 135.9693 | 125.3427 | 99.9815 | 15.9316 | 18.01 | 193.2031 | 122.7019 | 15.0103 | 33.8979 | 0.38206 | 77.1811 | 7.4482 | 0.11047 | 14.0322 | 0.088432 | 0.79547 | 0.79416
2025-06-02 17:00 | 33.9649 | 5.5622 | 0.7947 | 0.80762 | 18.5469 | 2.1889 | 12.8019 | 193.3613 | 17.9995 | 193.3508 | 26.0782 | 36.0235 | 14.5795 | 199.9186 | 23.9388 | 34.8346 | 14.1858 | 197.3731 | 21.1724 | 34.6201 | 14.3402 | 197.5079 | 21.6301 | 36.854 | 14.2868 | 197.8474 | 195.4751 | 13.3865 | 51.3006 | 0.51353 | 9.9705 | 0 | 80.2895 | 22.5965 | 38.2399 | 13.4856 | 191.6582 | 194.9221 | 13.1559 | 3.823 | 61.5229 | 12.8229 | 74.3458 | 15.9474 | 135.8034 | 125.3762 | 99.9785 | 15.9212 | 17.9995 | 193.3508 | 122.603 | 14.9997 | 33.8593 | 0.3877 | 76.9112 | 7.7528 | 0.11339 | 13.8105 | 0.087222 | 0.81547 | 0.77281
2025-06-02 18:00 | 33.9198 | 7.2316 | 0.79535 | 0.80706 | 18.3811 | 2.192 | 12.8182 | 193.3932 | 18.0105 | 193.3808 | 26.0286 | 36.0245 | 14.5787 | 199.9389 | 23.8838 | 34.8317 | 14.1923 | 197.3832 | 21.4785 | 34.4331 | 14.3611 | 197.6624 | 21.5924 | 36.2612 | 14.2923 | 197.8156 | 195.5008 | 13.3977 | 51.2204 | 0.54837 | 9.9708 | 0 | 80.3094 | 22.7188 | 36.9088 | 13.4904 | 191.6259 | 194.9342 | 13.1702 | 4.1318 | 61.3879 | 12.9636 | 74.3515 | 15.9501 | 135.7778 | 125.2778 | 99.9746 | 15.923 | 18.0105 | 193.3808 | 122.6021 | 15.0104 | 33.9372 | 0.38755 | 76.8193 | 7.8196 | 0.11804 | 13.7711 | 0.086618 | 0.8233 | 0.82237
2025-06-02 19:00 | 33.8053 | 7.5629 | 0.84133 | 0.85002 | 18.6183 | 2.1811 | 12.7488 | 193.1532 | 17.9642 | 193.2689 | 25.9594 | 36.1599 | 14.5403 | 199.844 | 23.9935 | 34.8298 | 14.1528 | 197.2724 | 21.4442 | 34.6554 | 14.3321 | 197.6544 | 21.4459 | 36.8147 | 14.2637 | 197.7873 | 195.302 | 13.3369 | 51.7507 | 0.5385 | 9.9713 | 0 | 80.312 | 22.7869 | 39.2684 | 13.4364 | 191.4505 | 194.7078 | 13.1078 | 3.872 | 61.7301 | 12.002 | 73.7321 | 15.9138 | 135.3303 | 125.2212 | 99.9714 | 15.8863 | 17.9642 | 193.2689 | 122.5192 | 14.9641 | 33.7382 | 0.38905 | 76.8735 | 8.9737 | 0.1224 | 14.8251 | 0.086214 | 0.82339 | 0.74622
2025-06-02 20:00 | 33.8601 | 7.2212 | 0.89384 | 0.89429 | 19.2335 | 2.1508 | 12.7673 | 193.2041 | 18.0043 | 193.1627 | 25.886 | 35.707 | 14.5903 | 199.9937 | 24.0887 | 34.8294 | 14.1954 | 197.3854 | 21.4412 | 35.032 | 14.3825 | 197.8116 | 21.6437 | 36.5624 | 14.3084 | 197.8532 | 195.3936 | 13.3685 | 52.1891 | 0.52007 | 9.97 | 0 | 80.2975 | 22.7103 | 44.0308 | 13.4799 | 191.5059 | 194.7969 | 13.1365 | 3.9978 | 61.7285 | 11.0974 | 72.8259 | 15.9416 | 135.4578 | 125.285 | 99.9703 | 15.9139 | 18.0043 | 193.1627 | 122.9925 | 15.0043 | 33.8826 | 0.39026 | 77.4446 | 9.1994 | 0.12282 | 15.528 | 0.086034 | 0.81478 | 0.8993
2025-06-02 21:00 | 33.9562 | 6.1721 | 0.86432 | 0.86442 | 19.2629 | 2.1762 | 12.8308 | 193.4353 | 18.0502 | 193.3294 | 25.8594 | 35.1039 | 14.6192 | 200.0809 | 24.0628 | 34.8294 | 14.2156 | 197.4471 | 21.779 | 34.4683 | 14.4012 | 197.9282 | 21.7523 | 34.556 | 14.3048 | 197.7595 | 195.5961 | 13.4259 | 51.8587 | 0.5205 | 9.9705 | 0 | 80.2847 | 22.6548 | 39.8874 | 13.5149 | 191.5825 | 194.9922 | 13.1889 | 3.8693 | 61.8786 | 12.0161 | 73.8947 | 15.9917 | 135.6039 | 125.8254 | 99.9707 | 15.9643 | 18.0502 | 193.3294 | 123.1771 | 15.0504 | 33.7895 | 0.39012 | 77.6781 | 5.8637 | 0.12067 | 14.4223 | 0.086045 | 0.78091 | 0.79426
2025-06-02 22:00 | 33.8695 | 5.3347 | 0.81267 | 0.82124 | 18.5832 | 2.1947 | 12.7708 | 193.229 | 17.9746 | 193.3665 | 25.8621 | 35.0896 | 14.5376 | 199.8325 | 24.0528 | 34.8286 | 14.1264 | 197.1755 | 21.2583 | 34.429 | 14.3009 | 197.62 | 21.5882 | 35.1504 | 14.2193 | 197.5012 | 195.355 | 13.3527 | 51.4348 | 0.53351 | 9.9732 | 0 | 80.2812 | 22.8226 | 36.9984 | 13.4358 | 191.3665 | 194.7455 | 13.1189 | 3.474 | 61.48 | 12.8543 | 74.3343 | 15.936 | 135.2753 | 125.7702 | 99.9718 | 15.9088 | 17.9746 | 193.3665 | 122.5661 | 14.9747 | 33.5013 | 0.38996 | 77.2033 | 5.2488 | 0.12038 | 14.0034 | 0.086098 | 0.75473 | 0.57777
2025-06-02 23:00 | 33.828 | 4.6233 | 0.81029 | 0.81155 | 18.0467 | 2.1687 | 12.7238 | 193.0712 | 17.9324 | 193.2252 | 25.8367 | 35.0882 | 14.5112 | 199.7645 | 24.0511 | 34.8265 | 14.1008 | 197.0907 | 20.8145 | 34.9499 | 14.2741 | 197.4019 | 21.7357 | 36.9458 | 14.2238 | 197.547 | 195.2007 | 13.3047 | 51.362 | 0.56482 | 9.9705 | 0 | 80.2731 | 22.9982 | 39.5516 | 13.3998 | 191.262 | 194.605 | 13.0752 | 3.5319 | 60.7815 | 12.5798 | 73.3613 | 15.8878 | 135.282 | 125.1842 | 99.9714 | 15.8604 | 17.9324 | 193.2252 | 122.3776 | 14.9325 | 33.7515 | 0.38456 | 76.7584 | 8.4177 | 0.12475 | 14.4373 | 0.085801 | 0.7566 | 0.5981
2025-06-03 | 34.3925 | 4.3912 | 0.86558 | 0.86696 | 17.684 | 2.0798 | 12.6265 | 192.7274 | 17.9048 | 193.1918 | 25.8106 | 35.0857 | 14.4789 | 199.6871 | 24.2678 | 34.8239 | 14.0719 | 196.7756 | 21.5962 | 34.9933 | 14.2548 | 197.3571 | 21.8933 | 37.9651 | 14.2159 | 197.6445 | 194.9843 | 13.2401 | 52.8412 | 0.56829 | 9.966 | 0 | 80.2321 | 22.9524 | 41.9987 | 13.3603 | 191.0701 | 194.3176 | 13.0017 | 3.6022 | 62.6226 | 8.9063 | 71.5289 | 15.8735 | 134.851 | 125.2181 | 99.9711 | 15.8455 | 17.9048 | 193.1918 | 122.0856 | 14.9051 | 33.7275 | 0.38346 | 75.9928 | 9.6079 | 0.13331 | 18.3061 | 0.085061 | 0.76176 | 0.44601
Total | MW: 813.204; MVAR: 129.6988; kg/s: 4474815.3638; kg/s: 299401.0551; kg/s: 5324811.9053; kg/s: 1006146.2728; kg/s: 6330958.1781; kg/s: 11681843.4887
Average | 33.8835 | 5.4041 | 0.85399 | 0.87406 | 19.158 | 2.1634 | 12.6903 | 192.9468 | 17.9573 | 193.0905 | 25.9255 | 34.7951 | 14.4811 | 199.6104 | 23.8345 | 34.5204 | 14.0885 | 197.0364 | 21.3339 | 34.9179 | 14.2393 | 197.1309 | 21.3123 | 37.8156 | 14.2033 | 197.5912 | 195.0926 | 13.2772 | 51.7918 | 0.48049 | 9.974 | 0 | 79.6502 | 22.2506 | 42.9071 | 13.4162 | 191.2884 | 194.5172 | 13.0568 | 3.4653 | 61.6298 | 11.6452 | 73.275 | 15.9149 | 135.2065 | 125.3566 | 99.9755 | 15.889 | 17.9573 | 193.0905 | 122.6219 | 14.9573 | 33.4946 | 0.39356 | 77.6586 | 6.977 | 0.12377 | 17.353 | 0.088129 | 0.78023 | 0.53108
Min | 32.6466 | 3.9269 | 0.7947 | 0.80706 | 17.684 | 2.0798 | 12.591 | 192.6043 | 17.7963 | 192.9103 | 25.6092 | 32.1407 | 14.3666 | 199.0356 | 23.423 | 33.0021 | 13.987 | 196.6567 | 20.8145 | 34.429 | 14.1016 | 196.5743 | 20.8977 | 34.556 | 14.0562 | 197.3049 | 194.7698 | 13.1771 | 49.7153 | 0.35571 | 9.966 | 0 | 78.6673 | 21.7064 | 36.9088 | 13.3414 | 190.9152 | 194.2117 | 12.9739 | 3.0951 | 59.7674 | 8.9063 | 71.5289 | 15.811 | 134.4736 | 124.8667 | 99.9604 | 15.7895 | 17.7963 | 192.9103 | 121.9315 | 14.7962 | 32.8666 | 0.34406 | 75.9928 | 4.6737 | 0.11028 | 12.1811 | 0.084714 | 0.67519 | 0.33551
Max | 34.5757 | 7.5629 | 0.89969 | 0.95128 | 20.6274 | 2.2878 | 12.8308 | 193.4353 | 18.0502 | 193.3808 | 26.4818 | 36.1599 | 14.6192 | 200.0809 | 24.2678 | 34.8393 | 14.2156 | 197.4471 | 21.779 | 35.0583 | 14.4012 | 197.9282 | 21.8933 | 40.067 | 14.3086 | 197.8989 | 195.5961 | 13.4259 | 53.122 | 0.56829 | 9.9874 | 0 | 80.312 | 22.9982 | 45.2111 | 13.5149 | 191.6694 | 194.9922 | 13.1889 | 4.1318 | 63.0895 | 14.9202 | 74.92 | 15.9917 | 135.9693 | 126.1008 | 99.9937 | 15.9643 | 18.0502 | 193.3808 | 123.518 | 15.0504 | 33.9372 | 0.44076 | 79.8243 | 9.6079 | 0.14322 | 23.2487 | 0.095073 | 0.83173 | 0.8993

## Running Hours (hidden)
DATE: | 2025-06-02
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0