## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-03
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 25.7982 | 199.7872 | 36.1416
|  | #6-2 | Production | 23.582 | 197.1341 | 35.2053
|  | #6-3 | Production | 21.0899 | 197.3519 | 35.9713
|  | #6-4 | Production | 21.8581 | 197.4677 | 36.2072
|  | #8-1 | Shut in | 0.58222 | 80.9614 | 9.9742
|  | #8-2 | Production | 22.644 | 191.3518 | 43.1123
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 53.058 | 4584212.6407
|  | PAD #8 - STEAM |  |  |  |  | 3.2464 | 280488.6408 | Online
|  | BRINE HEADER |  |  |  |  | 9.1554 | 791024.9826 | Offline
|  | TOTAL FLOW |  |  |  |  | 65.4598 | 5655726.2641
|  | PRESS SEPARATOR IJN 6 | Online | 13.2894 | 195.1263
|  | PRESS SEPARATOR IJN 8 | Online | 13.0541 | 194.4861
| INJECTION WELL | #5-1 | Injection | 15.8823 | 125.0432 | 99.9741 | 135.1606 | 11677878.9188
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.4585 |  |  | 827.0041
|  | NET | 31.7339 |  |  | 761.6127
| PARASITIC LOAD |  | 2.7246 |  |  | 65.3913
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 1.8997 |  |  | 6838.8131
|  | NET | 2.0628 |  |  | 7425.987
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
8. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 9. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
10. DHP tools pull out at Well IJN 9-1 and Well IJN8-1 was done by Toptek. Master valve and crown valve closed
11. Brine Dump Control valve Ijen-6 PV-2227A indication passing

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-03
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 761612.7324 |  | 0 |  | 761612.7324
|  |  |  | 761612.7324 |  | 0 |  | 761612.7324
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 761900 | [7 empty] | 761900
M-T-D GROSS GENERATION (kWHR) |  |  |  | 2466070 | [7 empty] | 2466070
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18395.12 | 0 | 5641.75 | 44.4 | 1496 | 1769 | 27346.27
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 54635.29 | -283254.3 | 16647.62 | 132.7 | 4493 | 5147 | 26420.32
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.4585 |  |  | 6.0684 |  | 19.2753
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 72
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 91.99%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 4584.2126 |  | 280.4886 |  |  | 5349.5153
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.053058 |  | 0.0032464 |  |  | 0.061916
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 791.025
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.0091554
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 6140.5403
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.071071
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 192.9177 |  |  |  | 192.8308
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.6836 |  |  |  | 17.9401
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 15.9173 |  | 23.2046 |  |  | 19.2753
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:07 | PLN Dispatch (Mr. Saputra Rahman) generation to 31.72 MW
0:08 | Start pit pump IJN 8 (Level pond: 32.1% / 6 stages) (22 barg / 128 A)
2:08 | Stop pit pump IJN 8 (Level pond: 27.8%)
2:09 | Start electrical pit pump IJN 6 (Level pond: 29.1%)
4:10 | Stop electrical pit pump IJN 6 (Level pond: 22.6%)
4:11 | Start pit pump IJN 8 (Level pond: 29.8%)
6:12 | Stop pit pump IJN 8 (Level pond: 25.4%)
6:13 | Start electrical pit pump IJN 6 (Level pond: 26.6%)
8:01 | Stop electrical pit pump IJN 6 (Level pond: 21.4%)
8:03 | PLN Dispatch (Mr. Rendy N) generation to 31.72 MW
8:15 | Safety standdown socialization by HSE team
8:30 | Daily tools box meeting
8:35 | Start pit pump IJN 8 (Level pond 28.3%)
10:45 | Top up fuel backhoe loader by MTC & Operation team
11:10 | Stop pit pump IJN 8 (Level pond 23.4%)
11:12 | Start electrical pit pump IJN 6 (Level pond 29.0%)
11:29 | Stroke test Master Valve & Release pressure body valve IJN 6-1
11:40 | Stroke test Master Valve & Release pressure body valve IJN 6-2
12:10 | Stroke test Master Valve & Release pressure body valve IJN 6-3
12:30 | Stroke test Master Valve & Release pressure body valve IJN 6-4
14:01 | PLN Dispatch (Mr. Rendy N) generation to 31.72 MW
14:09 | Switch control OHL 2 from local to remote
14:26 | Stop electrical pit pump IJN 6 (Level pond 19.6%)
14:27 | Start pit pump IJN 8 (Level pond 27.7%)
14:40 | Running test Brine booster pump A IJN 6 (Standart activities schedule)
14:57 | Top up oil engine EDG (Type oil : Mobil 7400)
15:21 | EDG unload run test (Standart activities schedule)
17:40 | Switching operation of Reinjection pump from pump B to pump A
18:00 | Stop pit pump IJN 8 (Level pond 20.2%)
19:33 | Start electrical pit pump IJN 6 (Level pond 28.4%)
19:45 | Handover day shift to night shift
21:15 | Power Block monitoring
21:45 | Stop electrical pit pump IJN 6 (Level pond 21.1%)
21:45 | Start pit pump IJN 8 (Level pond: 24%)
23:47 | Stop pit pump IJN 8 (Level pond: 20.7%)
23:48 | Start electrical pit pump IJN 6 (Level pond 24.1% / 5 stages) (Discharge pressure: 17.5 barg)
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Zakariya |  |  |  | CCR Operator : Ois |  |  |  | Steamfield : Dadan
Night Shift | Shift Leader : Hary |  |  |  | CCR Operator : Fauzan |  |  |  | Steamfield : Vandy
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-03
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2158700 | 2161700 | 3000 | 33850
(BACKUP) |  | 2126290 | 2157110 | 2160100 | 2990 | 33810
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 94603330 | 95365230 | 761900 | 2263320
(BACKUP) |  | 93082960 | 94583950 | 95345630 | 761680 | 2262670
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4183740 | 4221240 | 37500 | 79010
(BACKUP) |  | 4144060 | 4185590 | 4223100 | 37510 | 79040
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 102956935 | 103789325 | 832390 | 2466070
TOTAL |  |  |  |  | 832390 | 2466070
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 16759470 | 16907767 | 148297 | 377512
TOTAL |  |  |  |  | 148297 | 377512
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3125558.51 | 3143953.63 | 18395.12 | 54635.29
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1000764.28 | 1006406.03 | 5641.75 | 16647.62
U Ijen 5 |  | 7258.6 | 7346.9 | 7391.3 | 44.4 | 132.7
U Ijen 6 |  | 247889 | 250886 | 252382 | 1496 | 4493
U Ijen 8 |  | 299837 | 303215 | 304984 | 1769 | 5147
TOTAL |  |  |  |  | 27346.27 | 81055.61
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-03 01:00 | 34.5325 | 5.4714 | 0.85907 | 0.86354 | 17.3124 | 2.0744 | 12.6298 | 192.7392 | 17.8911 | 192.8961 | 25.9317 | 34.9012 | 14.4149 | 199.4989 | 24.0812 | 34.6389 | 14.0298 | 196.7731 | 21.7898 | 34.9994 | 14.2162 | 197.1553 | 21.726 | 36.5114 | 14.1527 | 197.3336 | 194.9366 | 13.2253 | 52.7457 | 0.5909 | 9.9742 | 0 | 80.1381 | 22.7258 | 44.6845 | 13.3786 | 191.1247 | 194.343 | 13.013 | 3.4718 | 62.0557 | 9.5774 | 71.6332 | 15.8498 | 134.6831 | 124.833 | 99.9658 | 15.8217 | 17.8911 | 192.8961 | 122.0065 | 14.8912 | 33.8467 | 0.38371 | 76.0014 | 7.4087 | 0.14678 | 15.7052 | 0.08453 | 0.76911 | 0.39846
2025-06-03 02:00 | 34.3856 | 4.7766 | 0.80027 | 0.80588 | 16.1883 | 2.0882 | 12.6118 | 192.6945 | 17.8371 | 192.884 | 25.9945 | 35.103 | 14.3391 | 199.2856 | 23.9648 | 34.8747 | 13.9529 | 196.5821 | 21.1164 | 35.0034 | 14.1239 | 196.7758 | 21.5799 | 35.0304 | 14.0563 | 196.9431 | 194.8097 | 13.1812 | 51.7413 | 0.62776 | 9.9708 | 0 | 80.0199 | 22.4961 | 45.1317 | 13.3414 | 191.0328 | 194.2641 | 12.986 | 3.2076 | 60.4654 | 11.3388 | 71.8042 | 15.8058 | 134.4073 | 124.7304 | 99.9613 | 15.7777 | 17.8371 | 192.884 | 121.7996 | 14.8371 | 33.7336 | 0.38362 | 75.7743 | 6.0075 | 0.15363 | 13.7225 | 0.084206 | 0.77221 | 0.39828
2025-06-03 03:00 | 34.2904 | 4.0293 | 0.76483 | 0.77114 | 15.9173 | 2.0928 | 12.6081 | 192.6576 | 17.8169 | 192.8581 | 25.979 | 35.5004 | 14.3412 | 199.2886 | 23.9999 | 35.3748 | 13.9565 | 196.6005 | 20.8289 | 35.0045 | 14.1197 | 196.7626 | 21.6922 | 35.0304 | 14.0625 | 196.9264 | 194.7363 | 13.1672 | 51.2773 | 0.63704 | 9.9645 | 0 | 79.904 | 22.4133 | 45.1573 | 13.3263 | 190.9801 | 194.2113 | 12.9767 | 3.0531 | 59.8646 | 11.8977 | 71.7623 | 15.7791 | 134.595 | 124.4674 | 99.9603 | 15.7508 | 17.8169 | 192.8581 | 121.5784 | 14.8167 | 33.8254 | 0.3849 | 75.3107 | 8.3408 | 0.14886 | 13.4263 | 0.084129 | 0.77197 | 0.39828
2025-06-03 04:00 | 34.4537 | 5.0681 | 0.77752 | 0.78413 | 16.3391 | 2.0783 | 12.6586 | 192.8346 | 17.8822 | 192.8504 | 25.9709 | 35.9313 | 14.4252 | 199.5584 | 23.9386 | 35.7998 | 14.052 | 196.8701 | 21.3668 | 35.0042 | 14.2195 | 197.1326 | 21.874 | 35.0293 | 14.1568 | 197.2234 | 194.9559 | 13.2336 | 51.6872 | 0.69174 | 9.9658 | 0 | 79.8166 | 22.4052 | 45.1626 | 13.3739 | 191.1128 | 194.403 | 13.0285 | 3.2567 | 60.492 | 11.1132 | 71.6051 | 15.8216 | 135.2866 | 124.1674 | 99.96 | 15.7926 | 17.8822 | 192.8504 | 121.6905 | 14.882 | 34.2236 | 0.3814 | 74.949 | 9.5031 | 0.14503 | 14.2144 | 0.084147 | 0.77488 | 0.44479
2025-06-03 05:00 | 34.7128 | 6.5285 | 0.78664 | 0.79512 | 16.4448 | 2.0625 | 12.7026 | 192.9942 | 17.9431 | 192.9899 | 25.9393 | 35.7948 | 14.4826 | 199.743 | 23.8843 | 35.4913 | 14.1151 | 197.0327 | 21.6472 | 35.0036 | 14.2808 | 197.3187 | 21.9108 | 35.028 | 14.2163 | 197.4176 | 195.1648 | 13.2937 | 52.0797 | 0.72378 | 9.9665 | 0 | 79.7413 | 22.4109 | 45.1532 | 13.4189 | 191.2484 | 194.5719 | 13.074 | 3.4877 | 61.2915 | 10.3029 | 71.5944 | 15.8743 | 135.5053 | 124.2499 | 99.9597 | 15.8451 | 17.9431 | 192.9899 | 121.7602 | 14.9429 | 34.4229 | 0.38171 | 74.5757 | 8.5084 | 0.14956 | 14.9173 | 0.083949 | 0.77777 | 0.41815
2025-06-03 06:00 | 34.4756 | 5.8725 | 0.81093 | 0.81835 | 17.6139 | 2.0553 | 12.6467 | 192.7984 | 17.8835 | 193.0043 | 25.8951 | 35.7965 | 14.4073 | 199.5282 | 23.9611 | 35.0465 | 14.0423 | 196.8398 | 21.1407 | 35.0122 | 14.1787 | 196.9914 | 21.9159 | 35.0378 | 14.1451 | 197.1908 | 194.953 | 13.2289 | 52.0675 | 0.7152 | 9.9707 | 0 | 79.7171 | 22.4191 | 45.148 | 13.3718 | 191.1538 | 194.3618 | 13.0188 | 3.2255 | 60.5779 | 10.2814 | 70.8593 | 15.8292 | 135.254 | 124.3165 | 99.9613 | 15.8001 | 17.8835 | 193.0043 | 121.8682 | 14.8832 | 34.141 | 0.39366 | 74.8662 | 7.531 | 0.14314 | 14.674 | 0.085352 | 0.77013 | 0.34955
2025-06-03 07:00 | 34.033 | 5.1357 | 0.85484 | 0.86862 | 20.1513 | 2.0885 | 12.5913 | 192.6061 | 17.8193 | 192.8215 | 25.8635 | 36.0488 | 14.3729 | 199.3906 | 23.8942 | 35.6503 | 13.9953 | 196.7426 | 20.826 | 35.5496 | 14.1009 | 196.8227 | 21.9031 | 35.6169 | 14.1096 | 197.085 | 194.7417 | 13.1673 | 52.0717 | 0.70991 | 9.982 | 0 | 79.9332 | 22.4449 | 45.108 | 13.3351 | 191.1529 | 194.1475 | 12.9633 | 2.9768 | 60.5305 | 10.5485 | 71.0789 | 15.7878 | 135.2625 | 124.6302 | 99.9709 | 15.7614 | 17.8193 | 192.8215 | 122.1215 | 14.8191 | 33.7397 | 0.39946 | 75.8545 | 9.1439 | 0.12295 | 14.4811 | 0.089865 | 0.73823 | 0.34738
2025-06-03 08:00 | 34.2964 | 6.3004 | 0.91299 | 0.93258 | 22.0031 | 2.0659 | 12.6607 | 192.8446 | 17.9325 | 192.6565 | 25.9091 | 35.5986 | 14.5619 | 199.8425 | 23.7952 | 36.2628 | 14.1798 | 197.2628 | 21.6093 | 35.8886 | 14.2851 | 197.4901 | 21.9092 | 36.7506 | 14.2872 | 197.6341 | 195.0914 | 13.2804 | 53.2925 | 0.6738 | 9.9846 | 0 | 80.3273 | 22.48 | 44.6233 | 13.4246 | 191.5217 | 194.4025 | 13.0358 | 3.1402 | 62.6692 | 8.1834 | 70.8525 | 15.8938 | 135.8962 | 124.9831 | 99.9836 | 15.8708 | 17.9325 | 192.6565 | 122.6307 | 14.9324 | 33.9444 | 0.38094 | 76.6012 | 11.0386 | 0.11609 | 16.8784 | 0.093839 | 0.68926 | 0.49783
2025-06-03 09:00 | 34.5915 | 7.8213 | 0.9627 | 0.98652 | 22.9606 | 2.0255 | 12.6831 | 192.8911 | 17.9888 | 192.6261 | 25.95 | 35.5852 | 14.6456 | 200.0244 | 23.7532 | 35.639 | 14.2855 | 197.5009 | 21.5853 | 35.9151 | 14.3776 | 197.7356 | 21.931 | 37.2121 | 14.3705 | 197.8605 | 195.2206 | 13.3307 | 54.2823 | 0.55048 | 9.98 | 0 | 80.7171 | 22.5005 | 43.6411 | 13.4571 | 191.6179 | 194.4649 | 13.061 | 3.238 | 63.5396 | 6.5252 | 70.0648 | 15.9529 | 135.9058 | 125.3944 | 99.9924 | 15.9309 | 17.9888 | 192.6261 | 123.0056 | 14.9886 | 33.9301 | 0.35329 | 77.3046 | 10.6477 | 0.12049 | 18.5853 | 0.095056 | 0.64947 | 0.50974
2025-06-03 10:00 | 34.4603 | 8.139 | 0.97068 | 0.99476 | 23.2046 | 2.0472 | 12.6744 | 192.8742 | 17.9683 | 192.6752 | 25.8175 | 36.5784 | 14.6455 | 199.9982 | 24.1441 | 35.0539 | 14.2784 | 197.3852 | 20.7556 | 36.5751 | 14.3622 | 197.5678 | 21.831 | 37.0987 | 14.3462 | 197.8117 | 195.1915 | 13.3193 | 54.0574 | 0.42377 | 9.9811 | 0 | 81.0658 | 22.5194 | 42.6775 | 13.4448 | 191.6148 | 194.4487 | 13.0482 | 3.2692 | 63.269 | 7.2777 | 70.5468 | 15.9544 | 135.4415 | 125.86 | 99.9953 | 15.9325 | 17.9683 | 192.6752 | 123.3111 | 14.9685 | 33.7202 | 0.3275 | 78.1344 | 10.2049 | 0.12075 | 18.1902 | 0.094495 | 0.63142 | 0.60923
2025-06-03 11:00 | 34.5459 | 7.4908 | 0.96467 | 0.98515 | 23.0342 | 2.0465 | 12.7569 | 193.1775 | 18.0527 | 192.6308 | 25.7327 | 37.0966 | 14.7547 | 200.3098 | 24.4511 | 35.0475 | 14.3662 | 197.6269 | 21.2701 | 36.7512 | 14.4737 | 197.8992 | 21.7435 | 36.8198 | 14.4194 | 198.0595 | 195.5116 | 13.4116 | 54.17 | 0.38223 | 9.9838 | 0 | 81.3454 | 22.5967 | 40.5286 | 13.5103 | 191.8015 | 194.7523 | 13.1245 | 3.4537 | 63.6147 | 7.0842 | 70.6989 | 16.031 | 135.7097 | 125.8693 | 99.9942 | 16.0091 | 18.0527 | 192.6308 | 123.4399 | 15.053 | 34.0022 | 0.32703 | 78.1896 | 9.3396 | 0.11851 | 18.2601 | 0.093553 | 0.61641 | 0.87836
2025-06-03 12:00 | 34.727 | 6.6901 | 0.94625 | 0.96389 | 22.4124 | 2.0409 | 12.801 | 193.3073 | 18.0958 | 192.6155 | 25.8316 | 37.0975 | 14.7926 | 200.4118 | 24.3804 | 35.0449 | 14.395 | 197.7808 | 21.4819 | 36.5918 | 14.5061 | 197.9663 | 21.7645 | 36.6507 | 14.4374 | 198.0928 | 195.6386 | 13.4563 | 54.2189 | 0.38754 | 9.9828 | 0 | 81.5091 | 22.7304 | 39.5733 | 13.5416 | 191.7962 | 194.878 | 13.1661 | 3.5056 | 63.8977 | 6.9777 | 70.8753 | 16.0675 | 135.7458 | 125.9332 | 99.993 | 16.0453 | 18.0958 | 192.6155 | 123.2931 | 15.0956 | 34.1753 | 0.32645 | 77.7416 | 7.7036 | 0.11546 | 18.3073 | 0.092626 | 0.61059 | 0.97965
2025-06-03 13:00 | 34.7061 | 7.4329 | 0.92081 | 0.93687 | 21.7344 | 2.046 | 12.7648 | 193.176 | 18.0523 | 192.8797 | 25.8192 | 37.0995 | 14.7235 | 200.2269 | 24.3768 | 35.0412 | 14.3317 | 197.6487 | 20.8148 | 36.8321 | 14.4318 | 197.6762 | 21.7698 | 36.8981 | 14.3779 | 197.9121 | 195.4794 | 13.409 | 53.808 | 0.43631 | 9.9828 | 0 | 81.5848 | 22.8264 | 40.7762 | 13.5097 | 191.6773 | 194.7488 | 13.133 | 3.2782 | 63.519 | 7.4907 | 71.0097 | 16.0277 | 135.5185 | 125.8736 | 99.9913 | 16.0048 | 18.0523 | 192.8797 | 122.9308 | 15.0521 | 34.1063 | 0.33006 | 77.2042 | 7.3859 | 0.11272 | 18.1689 | 0.091739 | 0.62518 | 0.65721
2025-06-03 14:00 | 34.5517 | 7.4307 | 0.91925 | 0.93588 | 21.8088 | 2.0421 | 12.6808 | 192.8918 | 17.9652 | 192.9704 | 25.6854 | 37.0975 | 14.6321 | 199.9389 | 24.0933 | 35.0401 | 14.2432 | 197.4008 | 20.8601 | 36.9837 | 14.3595 | 197.437 | 21.8399 | 37.0676 | 14.2978 | 197.6768 | 195.1719 | 13.3114 | 53.5836 | 0.48019 | 9.984 | 0 | 81.7468 | 22.8554 | 42.1068 | 13.4397 | 191.5204 | 194.4577 | 13.0504 | 3.0838 | 62.881 | 7.6785 | 70.5596 | 15.955 | 135.3807 | 125.6111 | 99.9935 | 15.9335 | 17.9652 | 192.9704 | 122.7821 | 14.965 | 33.9796 | 0.33549 | 77.076 | 8.747 | 0.1123 | 17.7918 | 0.092421 | 0.61214 | 0.30426
2025-06-03 15:00 | 34.6437 | 5.8464 | 0.91641 | 0.93505 | 21.7961 | 2.0357 | 12.7132 | 193.012 | 17.9971 | 192.7182 | 25.6818 | 36.7554 | 14.6757 | 200.0346 | 23.6277 | 34.7132 | 14.2709 | 197.4888 | 21.3378 | 36.866 | 14.4156 | 197.599 | 21.9137 | 36.9347 | 14.3252 | 197.762 | 195.2994 | 13.3483 | 53.7206 | 0.50892 | 9.9807 | 0 | 81.9263 | 22.8585 | 41.8255 | 13.4705 | 191.6002 | 194.5817 | 13.0803 | 3.3153 | 63.051 | 7.4739 | 70.5249 | 15.9785 | 135.6909 | 125.4269 | 99.9922 | 15.9582 | 17.9971 | 192.7182 | 123.0672 | 14.9972 | 34.2216 | 0.33242 | 77.0496 | 7.7425 | 0.11316 | 17.8104 | 0.092292 | 0.60303 | 0.6821
2025-06-03 16:00 | 34.7509 | 4.8708 | 0.88996 | 0.90857 | 21.3127 | 2.0474 | 12.7663 | 193.1908 | 18.04 | 192.7564 | 25.819 | 36.2483 | 14.7042 | 200.1293 | 23.2208 | 34.2194 | 14.2849 | 197.541 | 21.0324 | 36.8745 | 14.4376 | 197.6774 | 21.8895 | 36.9222 | 14.341 | 197.8092 | 195.4579 | 13.3999 | 53.5057 | 0.55057 | 9.9751 | 0 | 81.9816 | 22.8637 | 41.513 | 13.5073 | 191.6654 | 194.77 | 13.1317 | 3.3077 | 63.0749 | 8.0736 | 71.1485 | 16.0072 | 135.7811 | 125.4268 | 99.9849 | 15.9868 | 18.04 | 192.7564 | 122.9025 | 15.0401 | 34.3291 | 0.34754 | 76.5491 | 6.2193 | 0.11276 | 17.4298 | 0.090153 | 0.6405 | 0.85534
2025-06-03 17:00 | 34.6881 | 6.3711 | 0.84723 | 0.86129 | 19.8451 | 2.0528 | 12.742 | 193.1066 | 17.9978 | 192.9467 | 25.8218 | 36.0834 | 14.6373 | 199.9757 | 22.9646 | 34.0382 | 14.2173 | 197.3385 | 20.5403 | 37.0207 | 14.3823 | 197.4489 | 21.9014 | 37.0522 | 14.2874 | 197.6452 | 195.3221 | 13.3553 | 52.8836 | 0.53289 | 9.9715 | 0 | 81.9438 | 22.8451 | 42.6361 | 13.4614 | 191.5251 | 194.6763 | 13.1067 | 3.1643 | 62.1148 | 9.0942 | 71.2091 | 15.9724 | 135.5499 | 125.4473 | 99.9781 | 15.9505 | 17.9978 | 192.9467 | 122.5097 | 14.998 | 34.2482 | 0.35811 | 76.0888 | 7.3467 | 0.11392 | 16.2759 | 0.08798 | 0.68095 | 0.54114
2025-06-03 18:00 | 34.7323 | 7.6554 | 0.81514 | 0.82875 | 18.1263 | 2.0578 | 12.7676 | 193.2033 | 18.0167 | 193.0444 | 25.6209 | 36.091 | 14.6163 | 200.0495 | 22.9512 | 34.0166 | 14.2259 | 197.4145 | 20.9206 | 36.9238 | 14.4156 | 197.5492 | 21.9012 | 36.9484 | 14.3164 | 197.719 | 195.4146 | 13.3757 | 52.691 | 0.48385 | 9.9701 | 0 | 81.8254 | 22.817 | 41.4686 | 13.4646 | 191.5404 | 194.7661 | 13.1314 | 3.4277 | 62.0759 | 9.3949 | 71.4709 | 15.9704 | 135.6005 | 125.0038 | 99.9695 | 15.9439 | 18.0167 | 193.0444 | 122.218 | 15.0168 | 34.4699 | 0.36441 | 75.4277 | 8.4683 | 0.12745 | 15.8111 | 0.085941 | 0.69884 | 0.70772
2025-06-03 19:00 | 34.7682 | 7.2111 | 0.8098 | 0.82468 | 17.618 | 2.0569 | 12.7834 | 193.2646 | 18.0271 | 193.1053 | 25.6135 | 35.5798 | 14.586 | 200.042 | 22.9373 | 34.0113 | 14.2139 | 197.4164 | 21.2076 | 36.171 | 14.4069 | 197.6911 | 21.8455 | 36.2088 | 14.3042 | 197.6542 | 195.479 | 13.3919 | 52.7901 | 0.52451 | 9.9679 | 0 | 81.6758 | 22.847 | 38.5046 | 13.4648 | 191.5097 | 194.8126 | 13.1445 | 3.4717 | 62.3616 | 9.1518 | 71.5134 | 15.9689 | 135.3985 | 124.8176 | 99.9636 | 15.9397 | 18.0271 | 193.1053 | 121.9895 | 15.0271 | 34.5069 | 0.36665 | 74.8966 | 5.9972 | 0.14287 | 15.8341 | 0.084715 | 0.69444 | 0.89767
2025-06-03 20:00 | 34.4069 | 6.8693 | 0.82055 | 0.82923 | 17.841 | 2.0691 | 12.6891 | 192.9445 | 17.9215 | 193.0134 | 25.868 | 34.7357 | 14.451 | 199.6618 | 22.7584 | 34.1608 | 14.0836 | 197.0058 | 20.6377 | 36.1119 | 14.2729 | 197.3262 | 21.8437 | 36.2435 | 14.1806 | 197.2641 | 195.1093 | 13.2771 | 52.548 | 0.60444 | 9.9685 | 0 | 81.5473 | 22.8981 | 40.0171 | 13.3772 | 191.2103 | 194.4804 | 13.0509 | 3.1378 | 61.4627 | 9.7273 | 71.19 | 15.8907 | 134.8953 | 124.6899 | 99.9615 | 15.8614 | 17.9215 | 193.0134 | 121.8175 | 14.9216 | 34.1708 | 0.36365 | 75.2305 | 6.0009 | 0.14716 | 15.1146 | 0.084483 | 0.68695 | 0.58633
2025-06-03 21:00 | 34.2387 | 5.8072 | 0.82554 | 0.82684 | 17.151 | 2.0773 | 12.6273 | 192.7382 | 17.8603 | 192.839 | 25.8578 | 35.4844 | 14.3861 | 199.4747 | 22.6208 | 35.3039 | 14.0185 | 196.7655 | 20.6686 | 35.8476 | 14.2133 | 197.1185 | 21.9585 | 35.9784 | 14.1217 | 197.0712 | 194.8693 | 13.2027 | 52.3334 | 0.65585 | 9.9682 | 0 | 81.4024 | 22.8455 | 43.9769 | 13.3437 | 191.0783 | 194.3006 | 12.998 | 3.1107 | 60.7744 | 10.3506 | 71.1249 | 15.8446 | 134.5245 | 124.6026 | 99.9601 | 15.8151 | 17.8603 | 192.839 | 121.6512 | 14.8603 | 33.9972 | 0.35926 | 75.4529 | 8.5582 | 0.15741 | 14.5949 | 0.084184 | 0.69143 | 0.40781
2025-06-03 22:00 | 34.2512 | 4.7048 | 0.85124 | 0.85579 | 16.7761 | 2.0629 | 12.6438 | 192.7942 | 17.8898 | 192.7687 | 25.5964 | 36.7768 | 14.4168 | 199.5576 | 22.7668 | 36.5254 | 14.0409 | 196.8007 | 21.0349 | 34.9891 | 14.2273 | 197.2244 | 21.979 | 35.0297 | 14.1326 | 197.0878 | 194.9446 | 13.2264 | 53.058 | 0.67514 | 9.9648 | 0 | 81.2338 | 22.6827 | 45.0165 | 13.3723 | 191.1111 | 194.3796 | 13.0214 | 3.2458 | 61.0055 | 9.6524 | 70.6578 | 15.8654 | 134.3573 | 124.5772 | 99.96 | 15.8359 | 17.8898 | 192.7687 | 121.8679 | 14.8898 | 34.1149 | 0.36195 | 75.4538 | 7.6009 | 0.16573 | 14.9274 | 0.083948 | 0.69953 | 0.4077
2025-06-03 23:00 | 34.1089 | 4.3025 | 0.87699 | 0.88287 | 17.5326 | 2.07 | 12.6127 | 192.6855 | 17.8631 | 192.6878 | 25.6019 | 36.9922 | 14.3993 | 199.5027 | 22.7838 | 36.7525 | 14.0123 | 196.6917 | 20.8639 | 35.0074 | 14.1922 | 197.085 | 21.9741 | 35.372 | 14.1058 | 197.0068 | 194.8385 | 13.1949 | 54.3269 | 0.69568 | 9.9684 | 0 | 81.0691 | 22.5276 | 45.135 | 13.3383 | 190.9863 | 194.2719 | 12.9905 | 3.0725 | 61.1231 | 9.4819 | 70.605 | 15.8502 | 133.9287 | 124.8594 | 99.9612 | 15.8209 | 17.8631 | 192.6878 | 122.0401 | 14.863 | 33.9232 | 0.36346 | 75.8968 | 7.457 | 0.16159 | 14.8432 | 0.084142 | 0.69956 | 0.40832
2025-06-04 | 33.6527 | 3.8163 | 0.87095 | 0.86829 | 17.4829 | 2.1192 | 12.5915 | 192.598 | 17.8197 | 192.7011 | 25.3567 | 37.4213 | 14.3953 | 199.4198 | 22.6176 | 37.1797 | 14.0233 | 196.7093 | 20.82 | 36.384 | 14.2223 | 196.9954 | 21.9975 | 36.4999 | 14.1276 | 197.0374 | 194.6933 | 13.1579 | 54.4519 | 0.71086 | 9.9726 | 0 | 80.9022 | 22.4461 | 45.1309 | 13.3125 | 190.8613 | 194.1722 | 12.9639 | 3.0123 | 60.2647 | 11.0514 | 71.3161 | 15.8169 | 133.5364 | 125.2649 | 99.9636 | 15.787 | 17.8197 | 192.7011 | 122.171 | 14.8191 | 33.5372 | 0.36217 | 76.4427 | 16.4333 | 0.15891 | 12.2764 | 0.084372 | 0.6937 | 0.40887
Total | MW: 827.0041; MVAR: 145.6421; kg/s: 4584212.6407; kg/s: 280488.6408; kg/s: 5349515.3482; kg/s: 791024.9826; kg/s: 6140540.3307; kg/s: 11677878.9188
Average | 34.4585 | 6.0684 | 0.86564 | 0.87766 | 19.2753 | 2.0626 | 12.6836 | 192.9177 | 17.9401 | 192.8308 | 25.7982 | 36.1416 | 14.5336 | 199.7872 | 23.582 | 35.2053 | 14.1506 | 197.1341 | 21.0899 | 35.9713 | 14.3009 | 197.3519 | 21.8581 | 36.2072 | 14.2366 | 197.4677 | 195.1263 | 13.2894 | 53.058 | 0.58222 | 9.9742 | 0 | 80.9614 | 22.644 | 43.1123 | 13.4161 | 191.3518 | 194.4861 | 13.0541 | 3.2464 | 61.9157 | 9.1554 | 71.0711 | 15.9081 | 135.1606 | 125.0432 | 99.9741 | 15.8823 | 17.9401 | 192.8308 | 122.3522 | 14.94 | 34.0546 | 0.3612 | 76.1697 | 8.4723 | 0.13447 | 15.9267 | 0.088005 | 0.69157 | 0.54559
Min | 33.6527 | 3.8163 | 0.76483 | 0.77114 | 15.9173 | 2.0255 | 12.5913 | 192.598 | 17.8169 | 192.6155 | 25.3567 | 34.7357 | 14.3391 | 199.2856 | 22.6176 | 34.0113 | 13.9529 | 196.5821 | 20.5403 | 34.9891 | 14.1009 | 196.7626 | 21.5799 | 35.028 | 14.0563 | 196.9264 | 194.6933 | 13.1579 | 51.2773 | 0.38223 | 9.9645 | 0 | 79.7171 | 22.4052 | 38.5046 | 13.3125 | 190.8613 | 194.1475 | 12.9633 | 2.9768 | 59.8646 | 6.5252 | 70.0648 | 15.7791 | 133.5364 | 124.1674 | 99.9597 | 15.7508 | 17.8169 | 192.6155 | 121.5784 | 14.8167 | 33.5372 | 0.32645 | 74.5757 | 5.9972 | 0.1123 | 12.2764 | 0.083948 | 0.60303 | 0.30426
Max | 34.7682 | 8.139 | 0.97068 | 0.99476 | 23.2046 | 2.1192 | 12.801 | 193.3073 | 18.0958 | 193.1053 | 25.9945 | 37.4213 | 14.7926 | 200.4118 | 24.4511 | 37.1797 | 14.395 | 197.7808 | 21.7898 | 37.0207 | 14.5061 | 197.9663 | 21.9975 | 37.2121 | 14.4374 | 198.0928 | 195.6386 | 13.4563 | 54.4519 | 0.72378 | 9.9846 | 0 | 81.9816 | 22.8981 | 45.1626 | 13.5416 | 191.8015 | 194.878 | 13.1661 | 3.5056 | 63.8977 | 11.8977 | 71.8042 | 16.0675 | 135.9058 | 125.9332 | 99.9953 | 16.0453 | 18.0958 | 193.1053 | 123.4399 | 15.0956 | 34.5069 | 0.39946 | 78.1896 | 16.4333 | 0.16573 | 18.5853 | 0.095056 | 0.77777 | 0.97965

## Running Hours (hidden)
DATE: | 2025-06-03
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0