## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-04
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 25.7735 | 199.8128 | 36.3479
|  | #6-2 | Production | 22.9869 | 197.1499 | 36.3065
|  | #6-3 | Production | 21.0893 | 197.3137 | 35.775
|  | #6-4 | Production | 22.1209 | 197.812 | 36.0084
|  | #8-1 | Shut in | 0.76266 | 81.0598 | 9.9743
|  | #8-2 | Production | 22.6588 | 191.3577 | 42.8663
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 53.1525 | 4592379.8291
|  | PAD #8 - STEAM |  |  |  |  | 3.0677 | 265049.6529 | Online
|  | BRINE HEADER |  |  |  |  | 8.5688 | 740341.2732 | Offline
|  | TOTAL FLOW |  |  |  |  | 64.789 | 5597770.7552
|  | PRESS SEPARATOR IJN 6 | Online | 13.3063 | 195.1819
|  | PRESS SEPARATOR IJN 8 | Online | 13.0776 | 194.5501
| INJECTION WELL | #5-1 | Injection | 15.9072 | 125.0012 | 99.9706 | 134.9934 | 11663432.0179
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.4858 |  |  | 827.6582
|  | NET | 31.7316 |  |  | 761.5588
| PARASITIC LOAD |  | 2.7541 |  |  | 66.0994
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 1.8787 |  |  | 6763.3846
|  | NET | 2.0418 |  |  | 7350.4115
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
8. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 9. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
10. DHP tools pull out at Well IJN 9-1 and Well IJN8-1 was done by Toptek. Master valve and crown valve closed
11. Brine Dump Control valve Ijen-6 PV-2227A indication passing

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-04
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 761558.8213 |  |  |  | 761558.8213
|  |  |  | 761558.8213 |  | 0 |  | 761558.8213
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 761980 | [7 empty] | 761980
M-T-D GROSS GENERATION (kWHR) |  |  |  | 3293449 | [7 empty] | 3293449
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18134.96 | 0 | 5883.2 | 42.7 | 1434 | 1345 | 26839.86
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 72770.25 | -283254.3 | 22530.82 | 175.4 | 5927 | 6492 | 35125.22
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.4858 |  |  | 5.255 |  | 18.4129
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 96
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 91.99%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 4592.3798 |  | 265.0497 |  |  | 5225.5638
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.053153 |  | 0.0030677 |  |  | 0.060481
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 740.3413
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.0085688
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 5965.9051
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.06905
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 192.9944 |  |  |  | 192.7572
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.7074 |  |  |  | 17.9575
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 14.7898 |  | 20.6615 |  |  | 18.4129
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
1:49 | Stop electrical pit pump IJN 6 (Level pond: 19.6%)
1:50 | Start pit pump IJN 8 (Level pond: 22.8%)
3:51 | Stop pit pump IJN 8 (Level pond: 19.2%)
3:52 | Start electrical pit pump IJN 6 (Level pond: 22.6%)
5:53 | Stop electrical pit pump IJN 6 (Level pond: 19.1%)
5:54 | Start pit pump IJN 8 (Level pond: 21%)
7:15 | Drain steam trap on IJN 8 near instrument air receiver due to indicated hammering because line connected with brine line
7:55 | Stop pit pump IJN 8 (Level pond: 17.7%)
7:47 | Handover shift
8:20 | Tool Box Meeting
9:01 | Auto Start Seal oil pump OEC at pressure 5.29 bar
9:30 | Set the red needle indicator temperature setting for the GUST transformer 150 kV to match the HMI alarm settings: oil temperature at 90, HV winding at 105, and LV winding at 105 (with maintenance team)
10:00 | Emergency Eye Wash & Shower Inspection [standard activities shedule]
10:29 | Drain Suction Strainer A Booster Pump IJN 8 [standard activities shedule]
10:35 | Stroke test master valve well IJN 8-1 [standard activities shedule]
11:02 | Ormat team (shani) login to system for update logic MCC system
11:05 | Drain Suction Strainer A Booster Pump IJN 6 [standard activities shedule]
11:30 | Drain Brine Manifold Strainer A SP2501 inlet preheater [standard activities shedule]
12:29 | Start electrical pit pump IJN 6 (Level pond: 31.8%)
13:30 | Check fire systems (FM200) in the CCR, Relay room and Electric room [standard activities shedule]
14:30 | Inspection of fire alarm [standard activities shedule]
15:13 | Changeover Service water pump from P8201A to P8201B [standard activities shedule]
15:30 | First Aid Equipment Inspection [standard activities shedule]
16:55 | Stop Pit Pump IJN 6 (Level pond: 23.9%)
18:27 | Start pit pump IJN 8 (Level pond: 30.0%)
21:38 | Stop pit pump IJN 8 (Level pond : 24.9%)
21:39 | Start electrical pit pump IJN 6 (Level pond : 32.9%)
23:55 | Stop electrical pit pump IJN 6 (Level pond : 28.9%)
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Tio |  |  |  | Steamfield : Dede
Night Shift | Shift Leader : Zakariya |  |  |  | CCR Operator : Ois |  |  |  | Steamfield : Dadan
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-04
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2161700 | 2168100 | 6400 | 40250
(BACKUP) |  | 2126290 | 2160100 | 2166500 | 6400 | 40210
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 95365230 | 96127210 | 761980 | 3025300
(BACKUP) |  | 93082960 | 95345630 | 96107410 | 761780 | 3024450
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4221240 | 4242850 | 21610 | 100620
(BACKUP) |  | 4144060 | 4223100 | 4244720 | 21620 | 100660
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 103789325 | 104616704 | 827379 | 3293449
TOTAL |  |  |  |  | 827379 | 3293449
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 16907767 | 17035417 | 127650 | 505162
TOTAL |  |  |  |  | 127650 | 505162
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3143953.63 | 3162088.59 | 18134.96 | 72770.25
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1006406.03 | 1012289.23 | 5883.2 | 22530.82
U Ijen 5 |  | 7258.6 | 7391.3 | 7434 | 42.7 | 175.4
U Ijen 6 |  | 247889 | 252382 | 253816 | 1434 | 5927
U Ijen 8 |  | 299837 | 304984 | 306329 | 1345 | 6492
TOTAL |  |  |  |  | 26839.86 | 107895.47
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-04 01:00 | 34.3558 | 4.2828 | 0.81772 | 0.81743 | 17.236 | 2.0805 | 12.7056 | 193.0124 | 17.9337 | 192.9033 | 25.6899 | 35.6016 | 14.4568 | 199.6785 | 22.5338 | 35.5205 | 14.101 | 197.0108 | 21.4596 | 35.0178 | 14.2952 | 197.45 | 22.1218 | 35.0652 | 14.1832 | 197.2579 | 195.1486 | 13.2869 | 52.3996 | 0.69968 | 9.97 | 0 | 80.7488 | 22.5073 | 42.2428 | 13.4015 | 191.1727 | 194.5633 | 13.0706 | 3.1657 | 61.0514 | 10.4249 | 71.4763 | 15.9109 | 134.7102 | 125.0793 | 99.961 | 15.881 | 17.9337 | 192.9033 | 122.0244 | 14.9337 | 34.0574 | 0.36433 | 75.5666 | 7.7349 | 0.16038 | 14.3374 | 0.084133 | 0.69494 | 0.60424
2025-06-04 02:00 | 34.2192 | 3.7116 | 0.7568 | 0.7689 | 16.0902 | 2.0999 | 12.6473 | 192.8092 | 17.8498 | 193.0449 | 25.7765 | 34.9027 | 14.3274 | 199.2826 | 22.7865 | 34.8267 | 13.9771 | 196.672 | 20.8959 | 34.298 | 14.1476 | 197.0661 | 22.0389 | 34.3261 | 14.0485 | 196.8416 | 194.8838 | 13.2065 | 51.1898 | 0.70256 | 9.971 | 0 | 80.6232 | 22.5675 | 43.3029 | 13.3398 | 191.0416 | 194.3419 | 13.0083 | 3.0855 | 60.015 | 11.8429 | 71.8578 | 15.8396 | 134.6203 | 124.828 | 99.9596 | 15.8098 | 17.8498 | 193.0449 | 121.5121 | 14.8499 | 33.9697 | 0.36388 | 74.8926 | 5.0957 | 0.1631 | 13.2521 | 0.083863 | 0.69498 | 0.19955
2025-06-04 03:00 | 34.2571 | 2.9777 | 0.73225 | 0.74295 | 14.9251 | 2.0936 | 12.6431 | 192.7845 | 17.8396 | 192.8624 | 26.0461 | 34.2739 | 14.3269 | 199.2961 | 22.874 | 34.1948 | 13.9706 | 196.6162 | 20.6128 | 34.3487 | 14.1379 | 196.8867 | 22.1463 | 34.3858 | 14.0558 | 196.8397 | 194.8328 | 13.1943 | 50.881 | 0.72149 | 9.9701 | 0 | 80.4895 | 22.5497 | 45.0872 | 13.3416 | 191.0389 | 194.3342 | 13.0066 | 3.1716 | 59.522 | 12.1992 | 71.7213 | 15.8174 | 134.7965 | 124.3475 | 99.9587 | 15.7871 | 17.8396 | 192.8624 | 121.3006 | 14.8397 | 34.2433 | 0.36125 | 74.4503 | 7.0929 | 0.17579 | 12.8617 | 0.083447 | 0.70255 | 0.17854
2025-06-04 04:00 | 34.0626 | 4.3924 | 0.72784 | 0.73457 | 14.7898 | 2.0959 | 12.6148 | 192.6915 | 17.8011 | 192.8676 | 26.1304 | 33.6954 | 14.2773 | 199.1525 | 22.9914 | 33.3781 | 13.9381 | 196.5436 | 21.2402 | 34.5178 | 14.1207 | 196.7386 | 22.3166 | 34.5434 | 14.0328 | 196.759 | 194.7078 | 13.1557 | 50.661 | 0.70852 | 9.9661 | 0 | 80.3576 | 22.5138 | 45.0925 | 13.3103 | 190.9395 | 194.23 | 12.9768 | 3.0399 | 58.9688 | 12.4222 | 71.391 | 15.7791 | 134.7185 | 124.1917 | 99.9581 | 15.7488 | 17.8011 | 192.8676 | 121.3223 | 14.801 | 34.2373 | 0.36441 | 74.384 | 9.0919 | 0.18243 | 12.387 | 0.083214 | 0.71168 | 0.17851
2025-06-04 05:00 | 34.1915 | 4.9227 | 0.74008 | 0.74588 | 15.2034 | 2.0972 | 12.6488 | 192.8111 | 17.8456 | 192.9154 | 26.1012 | 33.5715 | 14.3052 | 199.242 | 23.0935 | 33.33 | 13.9784 | 196.7396 | 21.6728 | 35.0157 | 14.1671 | 196.8744 | 22.3531 | 35.0201 | 14.0775 | 196.9071 | 194.8598 | 13.2002 | 50.9216 | 0.69015 | 9.9678 | 0 | 80.2466 | 22.5077 | 45.0985 | 13.3416 | 191.0429 | 194.356 | 13.0114 | 3.0981 | 59.806 | 11.9001 | 71.7061 | 15.813 | 135.0386 | 124.2557 | 99.9584 | 15.7824 | 17.8456 | 192.9154 | 121.3568 | 14.8454 | 34.3807 | 0.36775 | 74.1348 | 8.0557 | 0.17813 | 12.7916 | 0.083334 | 0.71442 | 0.34088
2025-06-04 06:00 | 34.376 | 4.1436 | 0.76671 | 0.7731 | 16.5234 | 2.0764 | 12.6606 | 192.8545 | 17.8794 | 192.8859 | 26.1775 | 34.5699 | 14.3501 | 199.4008 | 23.0902 | 34.5542 | 14.0098 | 196.8699 | 21.3184 | 35.0917 | 14.1683 | 196.9252 | 22.3409 | 35.1023 | 14.1118 | 197.1081 | 194.9596 | 13.2279 | 51.5159 | 0.72804 | 9.972 | 0 | 80.2158 | 22.5152 | 45.097 | 13.3603 | 191.1685 | 194.4034 | 13.0269 | 3.0959 | 60.5747 | 10.8049 | 71.3796 | 15.8421 | 135.2517 | 124.3107 | 99.961 | 15.8107 | 17.8794 | 192.8859 | 121.4293 | 14.8793 | 34.433 | 0.37548 | 74.1253 | 6.2211 | 0.16394 | 13.8715 | 0.085152 | 0.70405 | 0.45701
2025-06-04 07:00 | 34.355 | 4.3984 | 0.80068 | 0.81373 | 18.2504 | 2.0752 | 12.6465 | 192.7783 | 17.8741 | 192.7992 | 26.0741 | 36.1707 | 14.4101 | 199.5438 | 22.91 | 36.074 | 14.0453 | 196.9074 | 20.8631 | 35.9003 | 14.1642 | 196.9919 | 22.2918 | 35.9566 | 14.1669 | 197.4126 | 194.9122 | 13.2228 | 52.0284 | 0.76769 | 9.9793 | 0 | 80.4187 | 22.5546 | 45.0717 | 13.3674 | 191.2464 | 194.3085 | 13.0147 | 3.0036 | 61.261 | 10.0341 | 71.2951 | 15.842 | 135.4408 | 124.3012 | 99.971 | 15.813 | 17.8741 | 192.7992 | 121.6873 | 14.874 | 34.3493 | 0.3809 | 74.6772 | 9.1826 | 0.13391 | 14.4116 | 0.089596 | 0.67347 | 0.57306
2025-06-04 08:00 | 34.6429 | 5.3825 | 0.83622 | 0.85283 | 19.2023 | 2.0618 | 12.755 | 193.1746 | 18.0007 | 192.7799 | 25.7657 | 36.8726 | 14.6214 | 200.0715 | 22.8246 | 36.7995 | 14.2357 | 197.4533 | 21.5268 | 36.3177 | 14.3567 | 197.6908 | 22.3428 | 36.3981 | 14.3631 | 198.2649 | 195.3952 | 13.3674 | 52.9207 | 0.78891 | 9.9781 | 0 | 80.7828 | 22.6423 | 41.0025 | 13.4778 | 191.6471 | 194.7094 | 13.1188 | 3.2051 | 62.5057 | 8.92 | 71.4258 | 15.9638 | 136.2913 | 124.6838 | 99.9832 | 15.9384 | 18.0007 | 192.7799 | 122.1649 | 15.0008 | 34.671 | 0.36631 | 74.7954 | 10.0896 | 0.11588 | 15.6341 | 0.093111 | 0.6464 | 0.86732
2025-06-04 09:00 | 34.491 | 5.8013 | 0.85746 | 0.87534 | 19.7224 | 2.0155 | 12.8496 | 193.5163 | 18.0805 | 193.0317 | 25.7097 | 37.0775 | 14.7207 | 200.3245 | 22.9348 | 37.008 | 14.3227 | 197.7188 | 21.5504 | 35.0627 | 14.4302 | 198.0263 | 22.2451 | 35.1194 | 14.4182 | 198.6245 | 195.7577 | 13.4738 | 53.1122 | 0.79776 | 9.9735 | 0 | 81.1245 | 22.8461 | 35.0355 | 13.549 | 191.9241 | 195.0097 | 13.2017 | 3.0937 | 61.2187 | 8.2993 | 69.518 | 16.0492 | 136.3416 | 125.0793 | 99.9885 | 16.0254 | 18.0805 | 193.0317 | 123.0535 | 15.0805 | 34.8202 | 0.34167 | 75.5586 | 5.9982 | 0.11875 | 15.4136 | 0.094205 | 0.61916 | 0.69054
2025-06-04 10:00 | 33.9723 | 5.5456 | 0.8607 | 0.88062 | 20.3704 | 2.0138 | 12.7927 | 193.2901 | 18.0083 | 193.2773 | 25.8777 | 37.0914 | 14.6598 | 200.0501 | 22.9666 | 37.008 | 14.2439 | 197.4255 | 20.6133 | 35.2184 | 14.3433 | 197.6398 | 22.0116 | 35.2893 | 14.3177 | 198.2848 | 195.4642 | 13.3959 | 52.4368 | 0.77122 | 9.9798 | 0 | 81.4129 | 23.0459 | 36.0416 | 13.512 | 191.8026 | 194.7602 | 13.1431 | 2.9166 | 59.6569 | 8.7556 | 68.4126 | 16.0179 | 135.438 | 126.0229 | 99.9879 | 15.9942 | 18.0083 | 193.2773 | 123.7076 | 15.0082 | 34.2802 | 0.30784 | 77.4433 | 7.1496 | 0.11901 | 15.0097 | 0.094348 | 0.58061 | 0.37955
2025-06-04 11:00 | 34.3445 | 4.8085 | 0.87558 | 0.89422 | 20.5993 | 2.0078 | 12.7362 | 193.0898 | 17.992 | 192.9899 | 25.7884 | 37.0922 | 14.6571 | 200.0145 | 23.0955 | 37.0052 | 14.2499 | 197.4056 | 21.1337 | 36.4411 | 14.3837 | 197.6474 | 22.1833 | 36.5196 | 14.3365 | 198.2844 | 195.2971 | 13.3484 | 53.0254 | 0.77834 | 9.9816 | 0 | 81.5756 | 23.0018 | 40.7258 | 13.4927 | 191.6895 | 194.6237 | 13.102 | 3.0961 | 61.2225 | 7.735 | 68.9575 | 16.0121 | 135.082 | 126.1882 | 99.9863 | 15.9884 | 17.992 | 192.9899 | 122.9057 | 14.9918 | 33.9727 | 0.30878 | 77.1209 | 11.3482 | 0.11599 | 16.3876 | 0.092826 | 0.58141 | 0.44665
2025-06-04 12:00 | 34.8006 | 4.4073 | 0.88995 | 0.90926 | 20.6615 | 1.9738 | 12.7635 | 193.1729 | 18.0363 | 192.8002 | 25.6912 | 37.0898 | 14.6884 | 200.1418 | 23.2185 | 37.0048 | 14.29 | 197.5478 | 21.6447 | 36.0101 | 14.4202 | 197.8735 | 22.2391 | 36.0738 | 14.3664 | 198.3976 | 195.4415 | 13.3937 | 53.8778 | 0.79593 | 9.983 | 0 | 81.6953 | 22.9027 | 39.6381 | 13.5072 | 191.6703 | 194.7033 | 13.1301 | 3.0757 | 61.8123 | 6.8786 | 68.6908 | 16.024 | 135.5281 | 125.2347 | 99.985 | 16.0003 | 18.0363 | 192.8002 | 122.4472 | 15.0361 | 34.4707 | 0.32465 | 75.8329 | 7.9468 | 0.11445 | 17.0984 | 0.092098 | 0.58621 | 0.44627
2025-06-04 13:00 | 34.6306 | 5.8011 | 0.8819 | 0.90276 | 20.5975 | 1.9578 | 12.7066 | 192.9845 | 17.9735 | 192.8615 | 25.7985 | 37.0893 | 14.6203 | 199.9413 | 23.1334 | 37.0041 | 14.2107 | 197.3264 | 20.7967 | 36.231 | 14.3206 | 197.5079 | 22.0342 | 36.29 | 14.2831 | 198.214 | 195.2301 | 13.3278 | 53.5948 | 0.79117 | 9.9848 | 0 | 81.8012 | 22.9046 | 40.8968 | 13.4557 | 191.5333 | 194.5225 | 13.0742 | 2.9993 | 60.4536 | 7.3463 | 67.7999 | 15.9721 | 135.2772 | 125.2687 | 99.9847 | 15.9481 | 17.9735 | 192.8615 | 122.5999 | 14.9735 | 34.3789 | 0.32399 | 75.9969 | 7.4127 | 0.11356 | 16.9035 | 0.091858 | 0.59337 | 0.37411
2025-06-04 14:00 | 34.7007 | 6.8203 | 0.86479 | 0.88191 | 20.303 | 1.9573 | 12.7449 | 193.0908 | 18.0055 | 192.836 | 25.777 | 37.0889 | 14.6617 | 200.051 | 23.3947 | 37.0012 | 14.2626 | 197.4276 | 20.8783 | 36.7867 | 14.3843 | 197.5304 | 22.1099 | 36.8482 | 14.3482 | 198.4659 | 195.3114 | 13.3591 | 53.3992 | 0.77676 | 9.9796 | 0 | 81.8573 | 22.8368 | 42.8406 | 13.497 | 191.6087 | 194.646 | 13.1158 | 3.1422 | 60.0998 | 7.8203 | 67.9201 | 15.9943 | 135.4663 | 125.2945 | 99.984 | 15.9701 | 18.0055 | 192.836 | 122.4641 | 15.0053 | 34.463 | 0.32561 | 75.8806 | 10.3048 | 0.11149 | 16.2586 | 0.090737 | 0.61864 | 0.62001
2025-06-04 15:00 | 34.864 | 6.016 | 0.83672 | 0.85072 | 19.6329 | 1.9518 | 12.8294 | 193.404 | 18.0761 | 193.0776 | 25.6779 | 37.0895 | 14.7095 | 200.224 | 23.3697 | 36.9985 | 14.31 | 197.6043 | 21.4083 | 35.486 | 14.4411 | 197.7993 | 22.0903 | 35.5406 | 14.3796 | 198.5693 | 195.6273 | 13.4453 | 53.3996 | 0.8093 | 9.9756 | 0 | 81.8739 | 22.824 | 37.5058 | 13.5375 | 191.7534 | 194.9088 | 13.1891 | 3.0366 | 59.7613 | 8.2853 | 68.0466 | 16.0476 | 135.813 | 125.2813 | 99.98 | 16.0226 | 18.0761 | 193.0776 | 122.5368 | 15.0761 | 34.7888 | 0.32893 | 75.3638 | 6.395 | 0.11155 | 15.823 | 0.08922 | 0.64071 | 0.63335
2025-06-04 16:00 | 34.6972 | 5.4997 | 0.84109 | 0.85102 | 19.0689 | 1.964 | 12.7188 | 193.0541 | 17.9754 | 193.0769 | 25.7175 | 37.0927 | 14.5797 | 199.93 | 22.985 | 36.997 | 14.1782 | 197.261 | 20.9122 | 35.6993 | 14.3167 | 197.5032 | 21.953 | 35.7453 | 14.2651 | 198.2148 | 195.2756 | 13.3286 | 53.3332 | 0.85701 | 9.9731 | 0 | 81.8271 | 22.8713 | 39.6369 | 13.432 | 191.4878 | 194.5901 | 13.0863 | 2.8627 | 60.0989 | 8.0462 | 68.1452 | 15.9624 | 135.1967 | 125.1327 | 99.9764 | 15.9365 | 17.9754 | 193.0769 | 122.0009 | 14.9756 | 34.3953 | 0.34526 | 74.847 | 7.4446 | 0.11425 | 15.8836 | 0.087457 | 0.66874 | 0.3958
2025-06-04 17:00 | 34.6967 | 6.6264 | 0.89534 | 0.91269 | 19.2453 | 1.9663 | 12.6656 | 192.8284 | 17.9567 | 192.5541 | 25.7252 | 37.0939 | 14.5649 | 199.8989 | 22.9619 | 36.9968 | 14.1781 | 197.2126 | 21.2056 | 36.9933 | 14.341 | 197.3975 | 22.0718 | 37.042 | 14.3002 | 198.4187 | 195.0919 | 13.286 | 54.5616 | 0.84112 | 9.9728 | 0 | 81.7316 | 22.7671 | 44.9812 | 13.3995 | 191.2701 | 194.4209 | 13.0474 | 3.0171 | 61.2303 | 6.9942 | 68.2246 | 15.925 | 134.9667 | 124.61 | 99.9735 | 15.8979 | 17.9567 | 192.5541 | 122.1308 | 14.9566 | 34.4905 | 0.35549 | 75.1963 | 11.0199 | 0.12157 | 16.9496 | 0.086361 | 0.68285 | 0.39335
2025-06-04 18:00 | 34.5985 | 6.7942 | 0.9163 | 0.95142 | 19.371 | 1.968 | 12.676 | 192.8933 | 17.9715 | 192.3279 | 25.574 | 37.0941 | 14.5473 | 199.8875 | 22.9778 | 36.9949 | 14.1653 | 197.2108 | 21.383 | 36.5078 | 14.3348 | 197.4842 | 22.0492 | 36.539 | 14.2767 | 198.3049 | 195.1755 | 13.3007 | 55.529 | 0.81342 | 9.9752 | 0 | 81.5709 | 22.669 | 43.0743 | 13.3912 | 191.2381 | 194.4724 | 13.0543 | 3.0811 | 61.2988 | 6.7914 | 68.0902 | 15.9438 | 134.378 | 125.115 | 99.9678 | 15.9159 | 17.9715 | 192.3279 | 122.5754 | 14.9715 | 34.4014 | 0.35573 | 75.8169 | 7.7499 | 0.13272 | 16.9917 | 0.085427 | 0.68906 | 0.39393
2025-06-04 19:00 | 34.3121 | 6.3342 | 0.89845 | 0.93811 | 19.0912 | 1.9641 | 12.6234 | 192.7415 | 17.9021 | 192.3963 | 25.599 | 37.0942 | 14.4627 | 199.6717 | 22.909 | 36.9908 | 14.0688 | 196.9314 | 20.5786 | 36.5132 | 14.2311 | 197.1754 | 21.9293 | 36.5271 | 14.175 | 197.8529 | 194.9803 | 13.232 | 55.319 | 0.81683 | 9.9718 | 0 | 81.4174 | 22.6527 | 43.1029 | 13.3405 | 191.0798 | 194.322 | 12.9992 | 2.989 | 59.9389 | 7.4543 | 67.3932 | 15.8985 | 133.7488 | 125.3263 | 99.9636 | 15.8704 | 17.9021 | 192.3963 | 122.4267 | 14.9023 | 34.0417 | 0.35139 | 76.0397 | 6.9812 | 0.14103 | 16.3371 | 0.08504 | 0.68957 | 0.39371
2025-06-04 20:00 | 34.3618 | 6.3338 | 0.88949 | 0.92634 | 18.7031 | 1.9638 | 12.6298 | 192.7253 | 17.9077 | 192.3794 | 25.6718 | 37.0942 | 14.4778 | 199.7055 | 22.8324 | 36.9679 | 14.0872 | 196.9217 | 20.8723 | 37.0095 | 14.2577 | 197.0654 | 21.9977 | 37.0247 | 14.21 | 197.56 | 194.9462 | 13.2333 | 55.4196 | 0.84475 | 9.9683 | 0 | 81.2388 | 22.6 | 45.4645 | 13.3592 | 191.0129 | 194.3204 | 13.0091 | 2.9945 | 59.7826 | 7.697 | 67.4796 | 15.8929 | 133.9952 | 125.0266 | 99.9625 | 15.8644 | 17.9077 | 192.3794 | 122.2071 | 14.9075 | 34.1874 | 0.35043 | 75.9254 | 9.499 | 0.14688 | 16.4203 | 0.084871 | 0.69079 | 0.39326
2025-06-04 21:00 | 34.6028 | 5.9504 | 0.88868 | 0.92456 | 18.4125 | 1.9186 | 12.6956 | 192.9686 | 17.9738 | 192.4416 | 25.5205 | 37.1749 | 14.5354 | 199.894 | 22.7316 | 36.9324 | 14.1471 | 197.1463 | 21.3688 | 36.2999 | 14.3133 | 197.1982 | 21.9843 | 36.7058 | 14.2649 | 197.4805 | 195.2033 | 13.3052 | 54.7839 | 0.83374 | 9.9694 | 0 | 80.9878 | 22.5243 | 44.9048 | 13.4319 | 191.2449 | 194.5666 | 13.0782 | 3.1727 | 58.9197 | 7.4675 | 66.3872 | 15.9466 | 134.3476 | 125.109 | 99.9616 | 15.9177 | 17.9738 | 192.4416 | 122.1344 | 14.9738 | 34.4535 | 0.35085 | 75.3694 | 8.0506 | 0.15149 | 16.1359 | 0.084719 | 0.69212 | 0.3932
2025-06-04 22:00 | 34.5455 | 6.2738 | 0.88542 | 0.92145 | 18.1377 | 1.9132 | 12.6715 | 192.9 | 17.9477 | 192.5295 | 25.3939 | 37.679 | 14.5111 | 199.8347 | 22.6974 | 37.3853 | 14.1096 | 197.0254 | 20.7544 | 35.2857 | 14.2439 | 196.8218 | 21.9148 | 36.7286 | 14.2171 | 197.4462 | 195.1255 | 13.2778 | 53.6847 | 0.73927 | 9.9712 | 0 | 80.7357 | 22.4273 | 46.0589 | 13.4153 | 191.2158 | 194.5104 | 13.0568 | 3.1664 | 58.8758 | 7.2179 | 66.0937 | 15.9249 | 134.1338 | 125.0951 | 99.9608 | 15.8961 | 17.9477 | 192.5295 | 122.0911 | 14.9478 | 34.3724 | 0.34935 | 75.129 | 6.8323 | 0.15405 | 15.8699 | 0.084649 | 0.69456 | 0.39362
2025-06-04 23:00 | 34.4561 | 5.4896 | 0.8841 | 0.91957 | 17.8937 | 1.9158 | 12.6585 | 192.8342 | 17.9374 | 192.4036 | 25.4495 | 37.5543 | 14.5181 | 199.8513 | 22.5795 | 37.8614 | 14.1166 | 196.9843 | 20.3711 | 35.6019 | 14.2481 | 196.7836 | 21.8945 | 37.7259 | 14.2355 | 197.5495 | 195.0444 | 13.2605 | 53.4128 | 0.63575 | 9.9729 | 0 | 80.4792 | 22.3092 | 48.6021 | 13.4155 | 191.1554 | 194.4651 | 13.0479 | 3.0798 | 59.2995 | 6.7101 | 66.0096 | 15.9101 | 134.161 | 124.9388 | 99.9602 | 15.8813 | 17.9374 | 192.4036 | 122.115 | 14.9372 | 34.3905 | 0.35026 | 75.2798 | 10.0473 | 0.15381 | 15.8992 | 0.084566 | 0.69802 | 0.39342
2025-06-05 | 35.1236 | 3.4059 | 0.91501 | 0.93409 | 17.8794 | 1.9296 | 12.8939 | 193.4544 | 18.211 | 192.1293 | 25.8295 | 35.1955 | 14.7621 | 200.4186 | 23.7928 | 36.5224 | 14.3997 | 197.6354 | 21.0819 | 36.9459 | 14.5578 | 197.4502 | 22.2421 | 37.6847 | 14.5195 | 198.4282 | 195.6948 | 13.5209 | 54.2538 | 0.5945 | 9.9771 | 0 | 80.2236 | 22.2698 | 48.2865 | 13.6605 | 191.5996 | 195.1136 | 13.2925 | 3.0362 | 64.1715 | 3.6029 | 67.7743 | 16.101 | 135.1004 | 125.3086 | 99.9603 | 16.0716 | 18.211 | 192.1293 | 123.0609 | 15.2094 | 35.214 | 0.34925 | 75.3183 | 12.6922 | 0.15621 | 19.0673 | 0.083874 | 0.69786 | 0.39332
Total | MW: 827.6582; MVAR: 126.1198; kg/s: 4592379.8291; kg/s: 265049.6529; kg/s: 5225563.7977; kg/s: 740341.2732; kg/s: 5965905.0708; kg/s: 11663432.0179
Average | 34.4858 | 5.255 | 0.84414 | 0.86348 | 18.4129 | 2.0026 | 12.7074 | 192.9944 | 17.9575 | 192.7572 | 25.7735 | 36.3479 | 14.5313 | 199.8128 | 22.9869 | 36.3065 | 14.1499 | 197.1499 | 21.0893 | 35.775 | 14.2969 | 197.3137 | 22.1209 | 36.0084 | 14.2481 | 197.812 | 195.1819 | 13.3063 | 53.1525 | 0.76266 | 9.9743 | 0 | 81.0598 | 22.6588 | 42.8663 | 13.4307 | 191.3577 | 194.5501 | 13.0776 | 3.0677 | 60.4811 | 8.5688 | 69.0498 | 15.9346 | 134.9934 | 125.0012 | 99.9706 | 15.9072 | 17.9575 | 192.7572 | 122.219 | 14.9574 | 34.3943 | 0.34849 | 75.381 | 8.3099 | 0.1396 | 15.4998 | 0.087421 | 0.66526 | 0.43888
Min | 33.9723 | 2.9777 | 0.72784 | 0.73457 | 14.7898 | 1.9132 | 12.6148 | 192.6915 | 17.8011 | 192.1293 | 25.3939 | 33.5715 | 14.2773 | 199.1525 | 22.5338 | 33.33 | 13.9381 | 196.5436 | 20.3711 | 34.298 | 14.1207 | 196.7386 | 21.8945 | 34.3261 | 14.0328 | 196.759 | 194.7078 | 13.1557 | 50.661 | 0.5945 | 9.9661 | 0 | 80.2158 | 22.2698 | 35.0355 | 13.3103 | 190.9395 | 194.23 | 12.9768 | 2.8627 | 58.8758 | 3.6029 | 66.0096 | 15.7791 | 133.7488 | 124.1917 | 99.9581 | 15.7488 | 17.8011 | 192.1293 | 121.3006 | 14.801 | 33.9697 | 0.30784 | 74.1253 | 5.0957 | 0.11149 | 12.387 | 0.083214 | 0.58061 | 0.17851
Max | 35.1236 | 6.8203 | 0.9163 | 0.95142 | 20.6615 | 2.0999 | 12.8939 | 193.5163 | 18.211 | 193.2773 | 26.1775 | 37.679 | 14.7621 | 200.4186 | 23.7928 | 37.8614 | 14.3997 | 197.7188 | 21.6728 | 37.0095 | 14.5578 | 198.0263 | 22.3531 | 37.7259 | 14.5195 | 198.6245 | 195.7577 | 13.5209 | 55.529 | 0.85701 | 9.9848 | 0 | 81.8739 | 23.0459 | 48.6021 | 13.6605 | 191.9241 | 195.1136 | 13.2925 | 3.2051 | 64.1715 | 12.4222 | 71.8578 | 16.101 | 136.3416 | 126.1882 | 99.9885 | 16.0716 | 18.211 | 193.2773 | 123.7076 | 15.2094 | 35.214 | 0.3809 | 77.4433 | 12.6922 | 0.18243 | 19.0673 | 0.094348 | 0.71442 | 0.86732

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6

## Running Hours (hidden)
DATE: | 2025-06-04
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0