## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-06
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 21.365 | 198.8437 | 36.1301
|  | #6-2 | Production | 22.9412 | 196.4826 | 36.9757
|  | #6-3 | Production | 20.8108 | 196.4149 | 37.358
|  | #6-4 | Production | 21.288 | 197.4341 | 38.4811
|  | #8-1 | Shut in | 1.4036 | 77.8822 | 9.9749
|  | #8-2 | Production | 21.8481 | 190.8952 | 48.6416
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 53.6454 | 4634960.5011
|  | PAD #8 - STEAM |  |  |  |  | 3.152 | 272330.6484 | Online
|  | BRINE HEADER |  |  |  |  | 7.935 | 685582.3909 | Offline
|  | TOTAL FLOW |  |  |  |  | 64.7323 | 5592873.5405
|  | PRESS SEPARATOR IJN 6 | Online | 13.1671 | 194.717
|  | PRESS SEPARATOR IJN 8 | Online | 12.9342 | 194.0776
| INJECTION WELL | #5-1 | Injection | 15.0034 | 124.1741 | 94.2982 | 131.5707 | 11367709.5535
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.3438 |  |  | 824.2519
|  | NET | 31.6493 |  |  | 759.5834
| PARASITIC LOAD |  | 2.6945 |  |  | 64.6685
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 1.8848 |  |  | 6785.3937
|  | NET | 2.0453 |  |  | 7363.0801
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
8. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 9. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
10. DHP tools pull out at Well IJN 9-1 and Well IJN8-1 was done by Toptek. Master valve and crown valve closed
11. Brine Dump Control valve Ijen-6 PV-2227A indication passing

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-06
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 759583.4209 |  |  |  | 759583.4209
|  |  |  | 759583.4209 |  | 0 |  | 759583.4209
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 761200 | [7 empty] | 761200
M-T-D GROSS GENERATION (kWHR) |  |  |  | 4952306 | [7 empty] | 4952306
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18560.62 | 0 | 6558.61 | 42.8 | 1323 | 1562 | 28047.03
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 110125.33 | -283254.3 | 35447.36 | 261.2 | 8736 | 9722 | 54166.56
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.3438 |  |  | 5.8524 |  | 19.2081
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 144
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 91.75%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 4634.9605 |  | 272.3306 |  |  | 5328.2467
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.053645 |  | 0.003152 |  |  | 0.06167
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 685.5824
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.007935
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 6013.8291
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.069605
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 192.4419 |  |  |  | 192.058
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.5478 |  |  |  | 17.8082
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 16.6926 |  | 22.7142 |  |  | 19.2081
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:09 | Start electrical pit pump IJN 6 (Level pond : 38.1%)
0:15 | Setting disharge pressure pit pump IJN 6 17.5 barg
3:10 | Stop electrical pit pump IJN 6 (Level pond : 29.8%)
3:15 | Start pit pump IJN 8 (Level pond : 30.7%)
6:00 | Stop pit pump IJN 8 (Level pond : 26.8%)
6:02 | Start electrical pit pump IJN 6 (Level pond : 30.9%)
6:31 | PLN RCC advised load dispatch at minimum (25MW) due to Grid system requirement (Long holiday) - PLN RCC (Mr. Rendy Nur Hidayatullah)
6:48 | Load was achieved at 25MW as PLN RCC dispatch - Confirmed to PLN
7:06 | Stop electrical pit pump IJN 6 (Level pond : 25.5%)
7:14 | PLN RCC advised load dispatch at 31.72 MW - PLN RCC (Mr. Gendhon hendro)
9:00 | Toolbox meeting
9:18 | Start pit pump IJN 8 (Level pond : 30.6%)
13:33 | Stop pit pump IJN 8 (Level pond : 25.3%)
13:34 | Start electrical pit pump IJN 6 (Level pond : 29.0%)
13:36 | Top up oil bearing in oil bottle glass Reinjection pump B from 5% to 95%
13:40 | Stroke test Control Valve steam Rockmuffler PV-2430A [standard activities schedule]
13:56 | Change priority Control Valve steam Rockmuffler from PV-2430B to PV-2430A [standard activities schedule]
14:15 | Stroke test Control Valve bypass reinjection pump PV-2605 [standard activities schedule]
14:30 | Inspection of Auxiliary Transformers (AT01, AT02, & AT03) [standard activities schedule]
16:45 | Stop electrical pit pump IJN 6 (Level pond : 14.7%)
16:56 | Start pit pump IJN 8 (Level pond : 30.1%)
19:48 | Stop pit pump IJN 8 (Level pond : 26.1%)
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Tio |  |  |  | Steamfield : Dede
Night Shift | Shift Leader : Zakariya |  |  |  | CCR Operator : Ois |  |  |  | Steamfield : Dadan
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-06
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2171390 | 2179400 | 8010 | 51550
(BACKUP) |  | 2126290 | 2169780 | 2177780 | 8000 | 51490
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 96889550 | 97650750 | 761200 | 4548840
(BACKUP) |  | 93082960 | 96869530 | 97630520 | 760990 | 4547560
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4272810 | 4308990 | 36180 | 166760
(BACKUP) |  | 4144060 | 4274690 | 4310870 | 36180 | 166810
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 105447397 | 106275561 | 828164 | 4952306
TOTAL |  |  |  |  | 828164 | 4952306
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 17175775 | 17316276 | 140501 | 786021
TOTAL |  |  |  |  | 140501 | 786021
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3180883.05 | 3199443.67 | 18560.62 | 110125.33
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1018647.16 | 1025205.77 | 6558.61 | 35447.36
U Ijen 5 |  | 7258.6 | 7477 | 7519.8 | 42.8 | 261.2
U Ijen 6 |  | 247889 | 255302 | 256625 | 1323 | 8736
U Ijen 8 |  | 299837 | 307997 | 309559 | 1562 | 9722
TOTAL |  |  |  |  | 28047.03 | 164291.89
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-06 01:00 | 34.326 | 1.9731 | 0.92171 | 0.94697 | 18.698 | 1.9901 | 12.601 | 192.6401 | 17.8932 | 192.1457 | 23.7408 | 35.354 | 14.3313 | 199.2576 | 23.0579 | 35.9037 | 14.0008 | 196.6494 | 20.654 | 36.9543 | 14.1584 | 196.8006 | 21.2909 | 37.0939 | 14.1061 | 197.8553 | 194.8916 | 13.213 | 53.3971 | 1.189 | 9.9707 | 0 | 77.7984 | 21.9427 | 46.425 | 13.3413 | 190.9328 | 194.2445 | 12.9812 | 3.047 | 61.5569 | 6.7539 | 68.3109 | 15.8822 | 133.5037 | 125.4268 | 99.9569 | 15.855 | 17.8932 | 192.1457 | 122.6014 | 14.8934 | 1.5658 | 39.9138 | 75.7951 | 1.0597 | 0.14362 | 17.152 | 0.084653 | 0.68221 | 0.40398
2025-06-06 02:00 | 34.4204 | 2.3992 | 0.90718 | 0.93517 | 18.3305 | 1.9724 | 12.608 | 192.6518 | 17.9008 | 192.0124 | 22.6841 | 36.2726 | 14.3073 | 199.1804 | 23.0938 | 35.9053 | 13.9997 | 196.6532 | 20.6782 | 36.9861 | 14.1613 | 196.7052 | 21.4693 | 37.4476 | 14.1139 | 197.6519 | 194.8844 | 13.2157 | 53.1995 | 1.143 | 9.9703 | 0 | 77.6624 | 21.9518 | 49.3804 | 13.3854 | 191.0511 | 194.3051 | 12.9997 | 3.0473 | 61.2395 | 6.6509 | 67.8904 | 15.8866 | 133.697 | 125.2973 | 99.9579 | 15.8591 | 17.9008 | 192.0124 | 122.2949 | 14.9008 | 1.5634 | 39.9509 | 75.5339 | 2.0013 | 0.14344 | 16.9007 | 0.084657 | 0.67818 | 0.40298
2025-06-06 03:00 | 34.7751 | 3.6675 | 0.90076 | 0.9286 | 18.0316 | 1.9606 | 12.6851 | 192.9199 | 17.9813 | 191.6336 | 22.1851 | 36.6596 | 14.3804 | 199.4109 | 23.0274 | 35.9056 | 14.0855 | 196.931 | 21.1421 | 36.9864 | 14.2574 | 196.9778 | 21.639 | 37.22 | 14.2036 | 197.963 | 195.184 | 13.3045 | 53.5346 | 1.0904 | 9.9723 | 0 | 77.5268 | 21.8396 | 50.0533 | 13.4695 | 191.3088 | 194.587 | 13.082 | 3.2103 | 61.8454 | 6.3336 | 68.179 | 15.9463 | 134.3003 | 125.0057 | 99.9581 | 15.9185 | 17.9813 | 191.6336 | 122.327 | 14.9813 | 1.5634 | 40.3274 | 75.0115 | 1.8906 | 0.1443 | 16.4176 | 0.08457 | 0.68022 | 0.40163
2025-06-06 04:00 | 34.7915 | 4.9285 | 0.87813 | 0.90713 | 17.9415 | 1.9789 | 12.6389 | 192.7653 | 17.9143 | 191.7269 | 21.9448 | 36.1618 | 14.3014 | 199.1719 | 22.9938 | 35.9056 | 14.0172 | 196.7296 | 20.9659 | 36.9868 | 14.1747 | 196.6571 | 21.6132 | 36.325 | 14.1275 | 197.8932 | 195.0233 | 13.254 | 53.3403 | 1.1219 | 9.9743 | 0 | 77.4009 | 21.7027 | 50.3182 | 13.399 | 191.1039 | 194.4075 | 13.0291 | 3.1932 | 61.82 | 7.0273 | 68.8474 | 15.8926 | 133.91 | 125.0921 | 99.9579 | 15.865 | 17.9143 | 191.7269 | 122.274 | 14.9142 | 1.5656 | 40.1264 | 75.0903 | 0.42485 | 0.14884 | 15.2487 | 0.084452 | 0.68623 | 0.4008
2025-06-06 05:00 | 34.9037 | 5.3428 | 0.7963 | 0.82673 | 16.6926 | 1.952 | 12.5856 | 192.5838 | 17.8307 | 192.1998 | 21.7528 | 36.0136 | 14.2095 | 198.893 | 23.0092 | 35.9047 | 13.9318 | 196.4695 | 20.5331 | 36.9611 | 14.0769 | 196.2789 | 21.619 | 36.0357 | 14.0417 | 197.6053 | 194.7784 | 13.1803 | 52.6588 | 1.212 | 9.9749 | 0 | 77.2979 | 21.6764 | 51.1635 | 13.3258 | 190.9105 | 194.1953 | 12.967 | 3.1028 | 59.8361 | 8.2962 | 68.1322 | 15.8248 | 133.5317 | 124.9893 | 99.9589 | 15.7973 | 17.8307 | 192.1998 | 121.3652 | 14.8305 | 1.5705 | 39.9375 | 74.2133 | 0.10627 | 0.15811 | 14.3007 | 0.084139 | 0.69373 | 0.39919
2025-06-06 06:00 | 33.564 | 4.1954 | 0.77152 | 0.80581 | 16.72 | 2.0832 | 12.6194 | 192.6897 | 17.65 | 192.2747 | 22.0507 | 33.9927 | 14.1237 | 198.6318 | 22.9878 | 34.6243 | 13.8709 | 196.3147 | 20.8563 | 34.6262 | 13.991 | 196.0933 | 21.9706 | 34.212 | 13.9698 | 197.426 | 194.777 | 13.1799 | 50.9066 | 1.2969 | 9.974 | 0 | 77.25 | 21.7772 | 47.7632 | 13.3399 | 190.9579 | 194.2604 | 12.9883 | 2.9858 | 58.4216 | 11.4984 | 69.92 | 15.2182 | 129.9611 | 123.9507 | 96.1116 | 15.165 | 17.65 | 192.2747 | 120.3352 | 14.657 | 1.5584 | 37.4873 | 73.8171 | 0.10683 | 0.15653 | 11.5882 | 0.085003 | 0.69219 | 1.4419
2025-06-06 07:00 | 31.8885 | 3.9838 | 0.82325 | 0.86369 | 18.6235 | 2.2658 | 12.696 | 192.9598 | 17.5077 | 192.1001 | 22.4623 | 32.8519 | 14.1386 | 198.6419 | 23.0205 | 34.363 | 13.8977 | 196.4144 | 20.818 | 33.2342 | 13.9736 | 196.0798 | 21.7451 | 34.2326 | 13.9844 | 197.3913 | 194.9595 | 13.2326 | 49.6003 | 1.3633 | 9.9751 | 0 | 77.3256 | 22.0017 | 42.5857 | 13.3964 | 191.1206 | 194.4656 | 13.0479 | 3.0452 | 58.6718 | 13.5815 | 72.2532 | 14.0703 | 124.9436 | 122.4225 | 69.1451 | 13.843 | 17.5077 | 192.1001 | 119.9768 | 14.5251 | 1.4139 | 33.5412 | 77.1584 | 1.3949 | 0.13194 | 10.3768 | 0.088355 | 0.67045 | 2.378
2025-06-06 08:00 | 33.1989 | 4.856 | 0.88348 | 0.93041 | 19.7902 | 2.1483 | 12.7518 | 193.1477 | 17.8007 | 192.2721 | 21.8536 | 35.6631 | 14.3902 | 199.3188 | 22.7468 | 36.666 | 14.1187 | 197.0038 | 21.0203 | 35.9028 | 14.2083 | 196.835 | 21.5354 | 37.7197 | 14.2293 | 197.7854 | 195.3001 | 13.3427 | 51.9332 | 1.3826 | 9.975 | 0 | 77.4848 | 22.1839 | 43.3796 | 13.4877 | 191.3969 | 194.7011 | 13.119 | 3.4281 | 61.2828 | 10.0386 | 71.3214 | 14.2509 | 129.1479 | 122.24 | 54.7704 | 14.0138 | 17.8007 | 192.2721 | 121.6931 | 14.8112 | 1.2482 | 35.829 | 79.1186 | 4.6121 | 0.11331 | 14.784 | 0.091425 | 0.61929 | 1.4473
2025-06-06 09:00 | 34.6829 | 5.7302 | 0.94624 | 1.0062 | 21.021 | 2.0259 | 12.7097 | 192.986 | 18.0371 | 192.6486 | 21.2185 | 36.8745 | 14.4991 | 199.6189 | 22.6031 | 37.952 | 14.2256 | 197.2868 | 21.5682 | 37.7558 | 14.3368 | 197.3048 | 21.6856 | 39.4804 | 14.3489 | 198.0181 | 195.3505 | 13.3658 | 54.5773 | 1.4108 | 9.9747 | 0 | 77.6865 | 22.1606 | 45.2146 | 13.4824 | 191.4088 | 194.6054 | 13.0962 | 3.3918 | 63.8575 | 6.4071 | 70.2646 | 15.0445 | 133.1173 | 124.432 | 64.1335 | 14.953 | 18.0371 | 192.6486 | 122.6852 | 15.0373 | 1.2019 | 38.3909 | 78.331 | 4.5753 | 0.11202 | 19.9571 | 0.093126 | 0.56148 | 0.51234
2025-06-06 10:00 | 34.731 | 6.5756 | 0.97399 | 1.0397 | 21.9309 | 2.0191 | 12.6933 | 192.9532 | 18.0414 | 192.5287 | 21.2178 | 36.1408 | 14.4884 | 199.5683 | 23.2818 | 37.9556 | 14.2304 | 197.2956 | 21.02 | 37.9216 | 14.3192 | 197.2209 | 21.5416 | 39.8281 | 14.3341 | 198.0838 | 195.3511 | 13.3614 | 54.9242 | 1.4333 | 9.9791 | 0 | 77.9316 | 22.1185 | 46.4806 | 13.4878 | 191.518 | 194.5845 | 13.084 | 3.2916 | 64.4911 | 5.6343 | 70.1254 | 15.1194 | 132.3473 | 125.3919 | 80.9843 | 15.0645 | 18.0414 | 192.5287 | 122.4211 | 15.0415 | 1.1829 | 37.7485 | 78.9005 | 2.7488 | 0.1132 | 21.2181 | 0.094307 | 0.52454 | 0.39717
2025-06-06 11:00 | 34.5316 | 7.3976 | 0.98537 | 1.0513 | 22.1662 | 2.0346 | 12.6416 | 192.773 | 17.9768 | 192.32 | 21.1583 | 36.1391 | 14.4306 | 199.3238 | 23.435 | 37.9581 | 14.1615 | 197.0075 | 20.6884 | 37.9875 | 14.2573 | 196.8875 | 21.4139 | 40.0712 | 14.2549 | 197.9069 | 195.1327 | 13.2969 | 54.535 | 1.4431 | 9.9853 | 0 | 78.142 | 22.023 | 49.3039 | 13.4548 | 191.4185 | 194.4269 | 13.0363 | 3.3207 | 64.1415 | 6.1153 | 70.2568 | 15.0665 | 132.1986 | 125.0286 | 98.6143 | 15.0445 | 17.9768 | 192.32 | 122.5906 | 14.9768 | 1.1676 | 37.7258 | 79.6602 | 2.9154 | 0.11367 | 20.1498 | 0.094399 | 0.50471 | 0.39116
2025-06-06 12:00 | 34.3891 | 7.8652 | 0.98732 | 1.058 | 22.3582 | 2.0487 | 12.5901 | 192.5771 | 17.916 | 192.2811 | 21.0674 | 36.1409 | 14.3573 | 199.0905 | 23.1433 | 37.9572 | 14.0826 | 196.7546 | 20.9748 | 37.9912 | 14.1884 | 196.5789 | 21.2255 | 40.0706 | 14.1764 | 197.6693 | 194.9055 | 13.2316 | 54.3435 | 1.3901 | 9.988 | 0 | 78.2985 | 21.8854 | 50.1214 | 13.3909 | 191.1865 | 194.2204 | 12.981 | 3.1987 | 63.8241 | 6.627 | 70.4512 | 15.0222 | 131.6039 | 124.9773 | 99.9884 | 15.003 | 17.916 | 192.2811 | 122.2614 | 14.916 | 1.164 | 37.4647 | 79.4182 | 2.5751 | 0.1135 | 19.6022 | 0.094153 | 0.50269 | 0.38425
2025-06-06 13:00 | 34.3116 | 7.7296 | 0.99944 | 1.0672 | 22.7142 | 2.0446 | 12.5827 | 192.5494 | 17.9164 | 192.2867 | 21.0328 | 36.1415 | 14.3608 | 199.0863 | 23.5983 | 37.9558 | 14.0917 | 196.7897 | 20.9786 | 37.9901 | 14.1831 | 196.5494 | 21.1195 | 40.3616 | 14.1793 | 197.5895 | 194.8897 | 13.2282 | 54.6081 | 1.3004 | 9.9875 | 0 | 78.4536 | 21.8481 | 50.1116 | 13.3831 | 191.2015 | 194.1947 | 12.9743 | 3.1314 | 64.0556 | 6.0984 | 70.154 | 15.016 | 131.7264 | 124.7629 | 99.9884 | 14.997 | 17.9164 | 192.2867 | 122.5 | 14.9166 | 1.1637 | 37.615 | 79.4824 | 2.3683 | 0.11369 | 20.0639 | 0.094548 | 2.4922 | 0.38701
2025-06-06 14:00 | 34.3407 | 7.495 | 1.0011 | 1.0614 | 22.363 | 2.0374 | 12.5751 | 192.5191 | 17.913 | 192.2495 | 21.0222 | 36.1411 | 14.3595 | 199.0543 | 23.6462 | 37.9562 | 14.0872 | 196.7609 | 20.6829 | 37.9864 | 14.193 | 196.4993 | 21.1844 | 40.869 | 14.1814 | 197.5231 | 194.8675 | 13.2216 | 54.6681 | 1.3364 | 9.9869 | 0 | 78.6106 | 21.8449 | 50.1021 | 13.3755 | 191.1979 | 194.1702 | 12.9656 | 3.1254 | 64.0733 | 5.8921 | 69.9654 | 15.0507 | 131.8754 | 125.0289 | 99.9895 | 15.0325 | 17.913 | 192.2495 | 122.8246 | 14.9133 | 1.1868 | 37.6226 | 79.9855 | 2.161 | 0.11314 | 20.2412 | 0.094384 | 2.4959 | 0.38857
2025-06-06 15:00 | 34.5674 | 7.3308 | 0.97267 | 1.0275 | 21.1774 | 2.0311 | 12.5516 | 192.4411 | 17.8933 | 192.2593 | 20.9673 | 36.1427 | 14.3229 | 198.9602 | 23.2476 | 37.9532 | 14.0415 | 196.644 | 20.7152 | 37.9901 | 14.1831 | 196.4542 | 21.1498 | 41.0782 | 14.1515 | 197.5129 | 194.8009 | 13.199 | 54.6264 | 1.4925 | 9.9822 | 0 | 78.6923 | 21.829 | 50.1067 | 13.3459 | 191.0804 | 194.099 | 12.9407 | 3.1847 | 64.0644 | 6.1466 | 70.2109 | 15.041 | 131.5665 | 125.2566 | 99.9849 | 15.0235 | 17.8933 | 192.2593 | 122.4424 | 14.8937 | 1.2336 | 37.3931 | 79.5872 | 1.7197 | 0.11118 | 20.1843 | 0.091992 | 0.52493 | 0.37865
2025-06-06 16:00 | 34.6954 | 7.1472 | 0.94893 | 0.99433 | 20.1888 | 2.0254 | 12.4829 | 192.204 | 17.8306 | 192.1896 | 20.9452 | 36.2544 | 14.2437 | 198.7506 | 23.2332 | 37.948 | 13.9684 | 196.4484 | 20.9521 | 38.1345 | 14.1301 | 196.3708 | 20.9404 | 41.0104 | 14.081 | 197.3143 | 194.5807 | 13.1333 | 54.8929 | 1.609 | 9.9747 | 0 | 78.6426 | 21.8036 | 50.1336 | 13.2663 | 190.8114 | 193.875 | 12.8745 | 3.3321 | 63.9778 | 6.2931 | 70.2709 | 14.9423 | 131.1535 | 124.6313 | 99.975 | 14.9239 | 17.8306 | 192.1896 | 121.5944 | 14.8305 | 1.267 | 37.2533 | 78.5244 | 1.9364 | 0.11044 | 20.3614 | 0.088765 | 0.57481 | 0.37166
2025-06-06 17:00 | 34.8784 | 7.3717 | 0.91727 | 0.95953 | 19.1027 | 2.0162 | 12.4106 | 191.9582 | 17.754 | 191.8697 | 20.9128 | 36.273 | 14.131 | 198.4985 | 23.2355 | 37.9447 | 13.8786 | 196.1934 | 20.9608 | 38.2043 | 14.0446 | 196.2234 | 20.8672 | 40.1528 | 13.9896 | 197.0848 | 194.3394 | 13.0567 | 55.5194 | 1.5798 | 9.9704 | 0 | 78.4806 | 21.7612 | 49.4354 | 13.1754 | 190.5229 | 193.6372 | 12.8054 | 3.102 | 63.4418 | 6.8784 | 70.3202 | 14.8492 | 131.053 | 123.8539 | 99.9656 | 14.8269 | 17.754 | 191.8697 | 120.9088 | 14.754 | 1.2852 | 37.3264 | 77.5465 | 1.468 | 0.12346 | 19.9357 | 0.086493 | 0.63058 | 0.37094
2025-06-06 18:00 | 34.7895 | 7.1223 | 0.88031 | 0.9145 | 17.9431 | 2.0068 | 12.4047 | 191.9549 | 17.7177 | 191.7415 | 20.8341 | 36.1256 | 14.0556 | 198.3774 | 22.8331 | 37.944 | 13.8154 | 196.0563 | 20.79 | 38.059 | 13.9848 | 196.1103 | 20.8176 | 39.2123 | 13.9273 | 196.9642 | 194.2892 | 13.0331 | 55.5683 | 1.5332 | 9.9689 | 0 | 78.2738 | 21.7281 | 48.4674 | 13.1516 | 190.4428 | 193.6212 | 12.797 | 2.7943 | 61.7974 | 8.0168 | 69.8142 | 14.7965 | 130.9676 | 123.5188 | 99.9587 | 14.7706 | 17.7177 | 191.7415 | 120.8963 | 14.7179 | 1.2967 | 37.4597 | 77.2321 | 0.40697 | 0.14593 | 18.3333 | 0.085196 | 0.6592 | 0.37322
2025-06-06 19:00 | 34.5392 | 6.2526 | 0.8588 | 0.88809 | 17.3488 | 2.004 | 12.4203 | 192.0012 | 17.7145 | 191.8822 | 20.7545 | 36.5341 | 14.041 | 198.3591 | 22.63 | 37.9285 | 13.8005 | 196.0161 | 20.5376 | 37.9863 | 13.9676 | 196.0382 | 20.8932 | 39.0681 | 13.9154 | 196.7703 | 194.2845 | 13.0343 | 54.7429 | 1.5492 | 9.966 | 0 | 78.0712 | 21.7175 | 49.1852 | 13.1631 | 190.4298 | 193.6568 | 12.8093 | 2.9791 | 60.6025 | 8.6142 | 69.2167 | 14.7862 | 131.1002 | 123.6543 | 99.9573 | 14.7593 | 17.7145 | 191.8822 | 120.8191 | 14.7144 | 1.3036 | 37.5081 | 76.9952 | 0.21456 | 0.15923 | 17.467 | 0.084579 | 0.67017 | 0.37341
2025-06-06 20:00 | 34.7539 | 5.2384 | 0.84268 | 0.88278 | 17.0819 | 1.996 | 12.4657 | 192.151 | 17.7643 | 191.8948 | 20.7245 | 36.9411 | 14.1042 | 198.5582 | 22.6531 | 37.7959 | 13.8634 | 196.1911 | 20.5126 | 37.9902 | 14.0366 | 196.2666 | 21.06 | 40.1213 | 14.0051 | 196.8984 | 194.4405 | 13.0849 | 54.4132 | 1.5876 | 9.9642 | 0 | 77.89 | 21.7172 | 50.0239 | 13.2099 | 190.518 | 193.8075 | 12.8553 | 3.2436 | 61.1626 | 8.2052 | 69.3678 | 14.817 | 131.4738 | 123.5386 | 99.9584 | 14.7898 | 17.7643 | 191.8948 | 120.5642 | 14.7642 | 1.3058 | 37.7362 | 76.3418 | 1.7328 | 0.16396 | 17.6038 | 0.084409 | 0.67246 | 0.37181
2025-06-06 21:00 | 34.9648 | 5.7723 | 0.82871 | 0.87317 | 16.969 | 1.9254 | 12.4551 | 192.1449 | 17.7235 | 191.848 | 20.7664 | 36.4319 | 14.0863 | 198.5194 | 22.4615 | 36.827 | 13.844 | 196.1643 | 20.7175 | 37.9908 | 14.0254 | 196.2513 | 21.1207 | 39.2245 | 13.9913 | 197.2449 | 194.453 | 13.0792 | 54.0422 | 1.5674 | 9.9654 | 0 | 77.7396 | 21.7172 | 49.0575 | 13.2008 | 190.5445 | 193.798 | 12.8453 | 3.3314 | 59.2755 | 8.0458 | 67.3214 | 14.7783 | 131.2802 | 123.1674 | 99.9598 | 14.7511 | 17.7235 | 191.848 | 119.9315 | 14.7236 | 1.3086 | 37.7314 | 75.3104 | 2.2333 | 0.16451 | 16.2288 | 0.084414 | 0.67371 | 0.37163
2025-06-06 22:00 | 34.5858 | 7.3364 | 0.83055 | 0.87309 | 17.4114 | 1.9437 | 12.2754 | 191.5229 | 17.5302 | 191.7876 | 20.6872 | 36.507 | 13.8806 | 197.8704 | 22.3185 | 35.9738 | 13.6339 | 195.4843 | 20.7123 | 37.9896 | 13.8073 | 195.5073 | 20.9201 | 36.6613 | 13.7522 | 196.8587 | 193.829 | 12.8909 | 53.2983 | 1.5333 | 9.9707 | 0 | 77.6106 | 21.7203 | 48.2294 | 13.0339 | 190.0535 | 193.1879 | 12.6677 | 3.1264 | 58.1607 | 9.065 | 67.2257 | 14.607 | 130.5958 | 122.6317 | 99.9606 | 14.5803 | 17.5302 | 191.7876 | 119.6411 | 14.5302 | 1.3083 | 37.399 | 75.2825 | 0.7147 | 0.1614 | 15.3195 | 0.084493 | 0.67205 | 0.37199
2025-06-06 23:00 | 34.0753 | 6.9368 | 0.84858 | 0.88331 | 17.9731 | 2.0058 | 12.2614 | 191.4504 | 17.5154 | 191.5122 | 20.5157 | 37.3209 | 13.859 | 197.7867 | 22.1448 | 36.4659 | 13.6058 | 195.3901 | 20.5514 | 37.9875 | 13.7743 | 195.3446 | 20.8232 | 37.0179 | 13.7256 | 196.5398 | 193.7055 | 12.8617 | 52.7727 | 1.5486 | 9.9738 | 0 | 77.5029 | 21.7082 | 49.1711 | 13.0225 | 189.9553 | 193.1135 | 12.6518 | 3.0284 | 58.5268 | 9.8201 | 68.3469 | 14.5814 | 130.7591 | 122.449 | 99.96 | 14.5548 | 17.5154 | 191.5122 | 120.2699 | 14.5153 | 1.3049 | 37.5725 | 76.0683 | 0.10664 | 0.15666 | 15.407 | 0.084668 | 0.66866 | 0.3722
2025-06-07 | 33.5472 | 5.8098 | 0.89306 | 0.90522 | 18.4177 | 2.1564 | 12.441 | 192.0608 | 17.6745 | 191.7269 | 20.2604 | 38.0446 | 14.0354 | 198.32 | 22.1863 | 37.7231 | 13.7862 | 195.9347 | 20.4278 | 37.9885 | 13.9515 | 195.9231 | 21.2677 | 39.0317 | 13.9327 | 196.8682 | 194.1897 | 13.0082 | 51.3859 | 1.5735 | 9.9722 | 0 | 77.3996 | 21.6963 | 51.1845 | 13.1878 | 190.4127 | 193.6968 | 12.8223 | 3.0063 | 59.9419 | 12.3998 | 72.3417 | 14.7175 | 131.8833 | 123.4311 | 99.9616 | 14.6907 | 17.6745 | 191.7269 | 121.2961 | 14.6751 | 1.3017 | 38.1896 | 76.6798 | 5.3784 | 0.1426 | 15.6843 | 0.085223 | 0.66086 | 0.37728
Total | MW: 824.2519; MVAR: 140.4581; kg/s: 4634960.5011; kg/s: 272330.6484; kg/s: 5328246.663; kg/s: 685582.3909; kg/s: 6013829.0539; kg/s: 11367709.5535
Average | 34.3438 | 5.8524 | 0.89989 | 0.94291 | 19.2081 | 2.028 | 12.5478 | 192.4419 | 17.8082 | 192.058 | 21.365 | 36.1301 | 14.2266 | 198.8437 | 22.9412 | 36.9757 | 13.96 | 196.4826 | 20.8108 | 37.358 | 14.0994 | 196.4149 | 21.288 | 38.4811 | 14.0718 | 197.4341 | 194.717 | 13.1671 | 53.6454 | 1.4036 | 9.9749 | 0 | 77.8822 | 21.8481 | 48.6416 | 13.3115 | 190.8952 | 194.0776 | 12.9342 | 3.152 | 61.6695 | 7.935 | 69.6045 | 15.0503 | 131.5707 | 124.1741 | 94.2982 | 15.0034 | 17.8082 | 192.058 | 121.5214 | 14.8097 | 1.3346 | 37.8854 | 77.1285 | 1.8688 | 0.13578 | 17.2719 | 0.088017 | 0.78715 | 0.56121
Min | 31.8885 | 1.9731 | 0.77152 | 0.80581 | 16.6926 | 1.9254 | 12.2614 | 191.4504 | 17.5077 | 191.5122 | 20.2604 | 32.8519 | 13.859 | 197.7867 | 22.1448 | 34.363 | 13.6058 | 195.3901 | 20.4278 | 33.2342 | 13.7743 | 195.3446 | 20.8176 | 34.212 | 13.7256 | 196.5398 | 193.7055 | 12.8617 | 49.6003 | 1.0904 | 9.9642 | 0 | 77.25 | 21.6764 | 42.5857 | 13.0225 | 189.9553 | 193.1135 | 12.6518 | 2.7943 | 58.1607 | 5.6343 | 67.2257 | 14.0703 | 124.9436 | 122.24 | 54.7704 | 13.843 | 17.5077 | 191.5122 | 119.6411 | 14.5153 | 1.1637 | 33.5412 | 73.8171 | 0.10627 | 0.11044 | 10.3768 | 0.084139 | 0.50269 | 0.37094
Max | 34.9648 | 7.8652 | 1.0011 | 1.0672 | 22.7142 | 2.2658 | 12.7518 | 193.1477 | 18.0414 | 192.6486 | 23.7408 | 38.0446 | 14.4991 | 199.6189 | 23.6462 | 37.9581 | 14.2304 | 197.2956 | 21.5682 | 38.2043 | 14.3368 | 197.3048 | 21.9706 | 41.0782 | 14.3489 | 198.0838 | 195.3511 | 13.3658 | 55.5683 | 1.609 | 9.988 | 0 | 78.6923 | 22.1839 | 51.1845 | 13.4878 | 191.518 | 194.7011 | 13.119 | 3.4281 | 64.4911 | 13.5815 | 72.3417 | 15.9463 | 134.3003 | 125.4268 | 99.9895 | 15.9185 | 18.0414 | 192.6486 | 122.8246 | 15.0415 | 1.5705 | 40.3274 | 79.9855 | 5.3784 | 0.16451 | 21.2181 | 0.094548 | 2.4959 | 2.378

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day
14 |  | Night
15 | 2025-06-08 | Day
16 |  | Night
17 | 2025-06-09 | Day
18 |  | Night
19 | 2025-06-10 | Day
20 |  | Night
21 | 2025-06-11 | Day
22 |  | Night
23 | 2025-06-12 | Day
24 |  | Night
25 | 2025-06-13 | Day
26 |  | Night
27 | 2025-06-14 | Day
28 |  | Night
29 | 2025-06-15 | Day
30 |  | Night
31 | 2025-06-16 | Day
32 |  | Night
33 | 2025-06-17 | Day
34 |  | Night
35 | 2025-06-18 | Day
36 |  | Night
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-06
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0