## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-07
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 20.1792 | 198.5398 | 37.3411
|  | #6-2 | Production | 22.604 | 196.1762 | 38.3625
|  | #6-3 | Production | 20.5262 | 196.25 | 38.1724
|  | #6-4 | Production | 20.6671 | 197.6201 | 40.5683
|  | #8-1 | Shut in | 1.8744 | 77.0836 | 9.973
|  | #8-2 | Production | 21.3113 | 190.6164 | 53.2157
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 53.9888 | 4664629.9267
|  | PAD #8 - STEAM |  |  |  |  | 3.3008 | 285188.4033 | Online
|  | BRINE HEADER |  |  |  |  | 6.3942 | 552461.2933 | Offline
|  | TOTAL FLOW |  |  |  |  | 63.6838 | 5502279.6232
|  | PRESS SEPARATOR IJN 6 | Online | 13.0787 | 194.4251
|  | PRESS SEPARATOR IJN 8 | Online | 12.841 | 193.7652
| INJECTION WELL | #5-1 | Injection | 14.8364 | 124.2548 | 99.9644 | 131.1365 | 11330197.8707
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.5597 |  |  | 829.4335
|  | NET | 31.8625 |  |  | 764.7001
| PARASITIC LOAD |  | 2.6972 |  |  | 64.7334
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 1.8427 |  |  | 6633.7804
|  | NET | 1.9987 |  |  | 7195.3434
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
8. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 9. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
10. DHP tools pull out at Well IJN 9-1 and Well IJN8-1 was done by Toptek. Master valve and crown valve closed
11. Brine Dump Control valve Ijen-6 PV-2227A indication passing

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-07
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 764700.0684 |  |  |  | 764700.0684
|  |  |  | 764700.0684 |  | 0 |  | 764700.0684
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 764000 | [7 empty] | 764000
M-T-D GROSS GENERATION (kWHR) |  |  |  | 5782740 | [7 empty] | 5782740
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18496.97 | 0 | 6396.94 | 44.7 | 986 | 1648 | 27572.61
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 128622.3 | -283254.3 | 41844.3 | 305.9 | 9722 | 11370 | 63242.2
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.5597 |  |  | 5.9286 |  | 19.5268
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 168
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 92.37%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 4664.6299 |  | 285.1884 |  |  | 5314.2413
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.053989 |  | 0.0033008 |  |  | 0.061507
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 552.4613
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.0063942
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 5866.7026
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.067902
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 192.0792 |  |  |  | 191.6648
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.4416 |  |  |  | 17.7716
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 17.9135 |  | 22.1392 |  |  | 19.5268
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:02 | PLN adviced load ROH 31.72 MW (Mr. Gendhon suhendro)
0:22 | Start pit pump IJN 8 (Level pond : 31.6%)
3:00 | Stop pit pump IJN 8 (Level pond : 26.9%)
4:37 | Start pit pump IJN 8 (Level pond : 29.1%)
6:15 | ACC fans inspection (Standart activities schedule) - result F-9370 little bit noisy from belt. The F-9313 noisy also. Overall all condition ACC is safe
7:25 | Stop pit pump IJN 8 (Level pond : 24.2%)
7:50 | Handover shift and Toolbox Meeting
9:18 | Start pit pump IJN 8 (Level pond : 27.1%)
9:28 | Running test Standby Brine Booster Pump P2201-A IJN 6 [standard activities schedule]
9:54 | Check and Release Pressure & Condensate Master Valve & Wing Valve Well IJN 6-1 [standard activities schedule]
10:07 | Check and Release Pressure & Condensate Master Valve & Wing Valve Well IJN 6-2 [standard activities schedule]
10:24 | Check and Release Pressure & Condensate Master Valve & Wing Valve Well IJN 6-3 [standard activities schedule]
10:41 | Check and Release Pressure & Condensate Master Valve & Wing Valve Well IJN 6-4 [standard activities schedule]
10:57 | Change over Generator Cooling water pump from P9813A to P9813B [standard activities schedule]
11:14 | Manual rotary Shaft pump Brine Booster Pump P2301-B IJN 8
11:21 | Check and Release Pressure & Condensate Master Valve & Wing Valve Well IJN 8-2 [standard activities schedule]
11:43 | Stroke test Dump valve LV2327-B IJN 8 [standard activities schedule]
11:46 | Change priority Dump valve from LV2327-A to LV2327-B IJN 8 [standard activities schedule]
13:18 | Stop pit pump IJN 8 (Level pond : 20.1%)
14:12 | Stroke test Control valve NV-2601B discharge Reinjection Pump B
14:14 | Running test Standby Reinjection pump P2601-B [standard activities schedule]
14:28 | Running test Fire Water Refilling pump P8202 [standard activities schedule]
14:43 | Running test Oil Sump Pump P8605 [standard activities schedule]
15:30 | Inspection of Auxiliary Transformers (AT IJN 6, AT IJN 8 and AT IJN 5) [standard activities schedule]
16:15 | Start Electrical pit pump IJN 6 (Level pond : 24.5%)
17:45 | Start Electrical pit pump IJN 6 (Level pond : 14.0%)
21:02 | PLN adviced load ROH 31.72 MW (Mr. Ilham ariyanto)
21:59 | Start pit pump IJN 8 (Level pond : 32.5%)
22:20 | PLN adviced load ROH 31.72 MW (Mr. Imam syamsudin)
23:55 | Stop pit pump IJN 8 (Level pond : 28.7%)
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Tio |  |  |  | Steamfield : Dede
Night Shift | Shift Leader : Zakariya |  |  |  | CCR Operator : Ois |  |  |  | Steamfield : Dadan
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-07
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2179400 | 2181710 | 2310 | 53860
(BACKUP) |  | 2126290 | 2177780 | 2180090 | 2310 | 53800
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 97650750 | 98414750 | 764000 | 5312840
(BACKUP) |  | 93082960 | 97630520 | 98394300 | 763780 | 5311340
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4308990 | 4339500 | 30510 | 197270
(BACKUP) |  | 4144060 | 4310870 | 4341400 | 30530 | 197340
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 106275561 | 107105995 | 830434 | 5782740
TOTAL |  |  |  |  | 830434 | 5782740
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 17316276 | 17458143 | 141867 | 927888
TOTAL |  |  |  |  | 141867 | 927888
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3199443.67 | 3217940.64 | 18496.97 | 128622.3
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1025205.77 | 1031602.71 | 6396.94 | 41844.3
U Ijen 5 |  | 7258.6 | 7519.8 | 7564.5 | 44.7 | 305.9
U Ijen 6 |  | 247889 | 256625 | 257611 | 986 | 9722
U Ijen 8 |  | 299837 | 309559 | 311207 | 1648 | 11370
TOTAL |  |  |  |  | 27572.61 | 191864.5
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-07 01:00 | 34.7736 | 5.4859 | 0.88865 | 0.91797 | 18.4214 | 1.9427 | 12.5182 | 192.347 | 17.8431 | 191.9726 | 20.324 | 38.042 | 14.1738 | 198.7606 | 22.4082 | 37.7623 | 13.921 | 196.3947 | 20.5567 | 37.9885 | 14.094 | 196.3729 | 21.1499 | 40.9909 | 14.0951 | 197.6442 | 194.6412 | 13.1419 | 53.6226 | 1.5768 | 9.9711 | 0 | 77.3262 | 21.5687 | 53.2202 | 13.3113 | 190.8345 | 194.0444 | 12.9222 | 3.2104 | 60.6934 | 6.8613 | 67.5547 | 14.8879 | 131.7861 | 124.0337 | 99.9597 | 14.8612 | 17.8431 | 191.9726 | 121.5222 | 14.843 | 1.2878 | 38.0027 | 76.9245 | 2.7774 | 0.14708 | 18.6268 | 0.085031 | 0.65516 | 0.37838
2025-06-07 02:00 | 34.6615 | 4.7893 | 0.88453 | 0.9112 | 18.2221 | 1.9373 | 12.4247 | 192.0456 | 17.7386 | 192.0833 | 20.2691 | 37.5391 | 14.0609 | 198.4219 | 22.3024 | 37.7626 | 13.8062 | 196.0372 | 20.7275 | 37.0387 | 13.97 | 195.9665 | 20.957 | 39.6231 | 13.9655 | 197.5523 | 194.3539 | 13.0479 | 53.527 | 1.6187 | 9.9726 | 0 | 77.2522 | 21.4072 | 53.258 | 13.2088 | 190.5602 | 193.7346 | 12.8262 | 3.207 | 59.7098 | 7.4385 | 67.1484 | 14.8142 | 130.9385 | 124.0981 | 99.9577 | 14.788 | 17.7386 | 192.0833 | 120.8103 | 14.7386 | 1.2913 | 37.446 | 76.5 | 1.2226 | 0.14786 | 18.0208 | 0.084897 | 0.65732 | 0.37525
2025-06-07 03:00 | 34.2032 | 3.606 | 0.88151 | 0.90172 | 17.9135 | 2.0082 | 12.364 | 191.8179 | 17.6427 | 191.9041 | 20.2358 | 37.0613 | 13.9654 | 198.1143 | 22.2057 | 37.7628 | 13.7091 | 195.7121 | 20.5218 | 36.0446 | 13.857 | 195.4995 | 20.8104 | 39.1211 | 13.8566 | 197.1342 | 194.0737 | 12.9689 | 52.8009 | 1.6894 | 9.9732 | 0 | 77.1614 | 21.3318 | 53.2609 | 13.1411 | 190.3175 | 193.4945 | 12.7601 | 3.1746 | 59.6019 | 9.0833 | 68.6852 | 14.7185 | 130.8147 | 123.5592 | 99.9569 | 14.6922 | 17.6427 | 191.9041 | 120.8246 | 14.6425 | 1.2972 | 37.4704 | 76.7292 | 0.1067 | 0.14884 | 16.3954 | 0.084748 | 0.66107 | 0.37196
2025-06-07 04:00 | 34.137 | 3.5849 | 0.87187 | 0.89758 | 17.9197 | 2.0301 | 12.4423 | 192.069 | 17.7223 | 191.8676 | 20.2229 | 37.5424 | 14.0518 | 198.3755 | 22.4029 | 37.7633 | 13.8013 | 195.9602 | 20.4376 | 36.9728 | 13.9573 | 195.7444 | 20.9044 | 40.0463 | 13.9675 | 197.4563 | 194.2894 | 13.0402 | 52.5623 | 1.7679 | 9.9702 | 0 | 77.0439 | 21.3174 | 53.2684 | 13.2121 | 190.4712 | 193.7355 | 12.8353 | 3.1536 | 60.2504 | 9.0528 | 69.3032 | 14.7806 | 131.1449 | 123.818 | 99.9561 | 14.7537 | 17.7223 | 191.8676 | 121.319 | 14.7221 | 1.2981 | 37.7735 | 77.1158 | 2.2414 | 0.15198 | 16.7652 | 0.084601 | 0.66189 | 0.37116
2025-06-07 05:00 | 34.7016 | 5.0649 | 0.86869 | 0.90723 | 18.0503 | 1.8961 | 12.4976 | 192.2831 | 17.82 | 191.9038 | 20.2226 | 37.7891 | 14.1516 | 198.7025 | 22.5043 | 37.7671 | 13.9058 | 196.2847 | 21.143 | 37.9734 | 14.0844 | 196.24 | 20.9953 | 40.0437 | 14.082 | 197.9801 | 194.5796 | 13.1208 | 53.5009 | 1.8205 | 9.9699 | 0 | 76.9421 | 21.3163 | 53.2659 | 13.2711 | 190.6733 | 193.9559 | 12.8946 | 3.3399 | 58.7679 | 7.0297 | 65.7976 | 14.8736 | 131.2623 | 124.1151 | 99.9558 | 14.8467 | 17.82 | 191.9038 | 121.237 | 14.8202 | 1.2918 | 37.8888 | 76.6158 | 3.0024 | 0.15249 | 18.6599 | 0.084696 | 0.65839 | 0.37351
2025-06-07 06:00 | 34.8496 | 5.5985 | 0.87873 | 0.9223 | 18.3942 | 1.8632 | 12.4501 | 192.1256 | 17.7832 | 191.8131 | 20.226 | 37.3086 | 14.1095 | 198.5696 | 22.3471 | 37.7672 | 13.86 | 196.1116 | 21.0168 | 38.0045 | 14.0294 | 196.125 | 20.8986 | 40.0459 | 14.0321 | 197.8285 | 194.4677 | 13.0839 | 53.9526 | 1.7273 | 9.9733 | 0 | 76.8813 | 21.3245 | 53.2675 | 13.2353 | 190.588 | 193.8102 | 12.8506 | 3.3025 | 58.3595 | 6.5707 | 64.9301 | 14.8435 | 131.039 | 123.7109 | 99.9575 | 14.8171 | 17.7832 | 191.8131 | 121.0661 | 14.7835 | 1.2734 | 37.8511 | 76.3594 | 0.98538 | 0.1453 | 19.1788 | 0.085675 | 0.65018 | 0.37915
2025-06-07 07:00 | 34.3253 | 6.0527 | 0.88485 | 0.92978 | 19.0135 | 1.9873 | 12.3719 | 191.8493 | 17.6794 | 191.8356 | 20.1963 | 37.0659 | 14.0103 | 198.2336 | 22.3519 | 37.7717 | 13.7567 | 195.7452 | 20.2569 | 38.0158 | 13.8944 | 195.6802 | 20.8727 | 40.0544 | 13.9307 | 197.4939 | 194.1494 | 12.9904 | 53.312 | 1.561 | 9.976 | 0 | 76.8786 | 21.3338 | 53.2502 | 13.1662 | 190.4008 | 193.5311 | 12.7699 | 3.1611 | 60.2915 | 7.9232 | 68.2147 | 14.763 | 130.6454 | 123.7579 | 99.9625 | 14.738 | 17.6794 | 191.8356 | 121.2662 | 14.6796 | 1.2302 | 37.6027 | 76.9474 | 1.1531 | 0.12865 | 18.2317 | 0.088015 | 0.62985 | 0.38218
2025-06-07 08:00 | 34.1487 | 6.9111 | 0.89189 | 0.94143 | 19.6823 | 2.0374 | 12.3624 | 191.7986 | 17.6673 | 191.7521 | 20.1826 | 37.123 | 14.0227 | 198.2058 | 22.5651 | 37.7924 | 13.7639 | 195.7254 | 20.4987 | 38.0798 | 13.8901 | 195.6182 | 20.8711 | 40.061 | 13.9397 | 197.5291 | 194.0943 | 12.9823 | 53.1003 | 1.5191 | 9.9764 | 0 | 76.9377 | 21.3389 | 53.2202 | 13.1624 | 190.3716 | 193.4766 | 12.7595 | 3.2826 | 61.7296 | 7.8443 | 69.5738 | 14.7619 | 130.7353 | 124.0474 | 99.967 | 14.7386 | 17.6673 | 191.7521 | 121.435 | 14.6673 | 1.183 | 37.5302 | 77.4671 | 2.7631 | 0.11403 | 18.0838 | 0.090331 | 0.5993 | 0.378
2025-06-07 09:00 | 34.5066 | 7.1991 | 0.89174 | 0.94463 | 19.7751 | 1.9183 | 12.3814 | 191.8678 | 17.7067 | 191.6437 | 20.1636 | 37.6214 | 14.084 | 198.3486 | 22.6203 | 37.805 | 13.8165 | 195.866 | 20.9546 | 38.576 | 13.957 | 195.7979 | 20.8527 | 40.0646 | 13.9831 | 197.6808 | 194.2117 | 13.0182 | 53.6197 | 1.589 | 9.9742 | 0 | 77.0136 | 21.3304 | 53.1997 | 13.1854 | 190.452 | 193.5511 | 12.7806 | 3.2673 | 59.753 | 6.4416 | 66.1946 | 14.8024 | 131.081 | 124.0693 | 99.9693 | 14.7801 | 17.7067 | 191.6437 | 121.2836 | 14.7068 | 1.175 | 37.6456 | 77.3209 | 2.5752 | 0.11087 | 19.0626 | 0.091163 | 0.58791 | 0.3701
2025-06-07 10:00 | 34.731 | 7.3029 | 0.88487 | 0.93705 | 19.5986 | 1.8588 | 12.3766 | 191.8638 | 17.7085 | 191.618 | 20.1525 | 38.067 | 14.0944 | 198.3638 | 22.5622 | 37.806 | 13.8209 | 195.9099 | 20.7841 | 39.0179 | 13.9641 | 195.8358 | 20.8416 | 40.0658 | 13.9716 | 197.6234 | 194.2332 | 13.0207 | 53.9857 | 1.7076 | 9.9742 | 0 | 77.0842 | 21.3244 | 53.1924 | 13.1837 | 190.4952 | 193.5514 | 12.7764 | 3.1605 | 58.6798 | 5.8776 | 64.5574 | 14.8025 | 131.1544 | 123.7926 | 99.9708 | 14.7806 | 17.7085 | 191.618 | 121.2028 | 14.7085 | 1.1825 | 37.7469 | 77.2022 | 1.4011 | 0.11037 | 19.4116 | 0.091271 | 0.58915 | 0.36688
2025-06-07 11:00 | 34.273 | 6.4161 | 0.91372 | 0.96364 | 20.2923 | 1.969 | 12.3863 | 191.8878 | 17.7059 | 191.6517 | 20.1566 | 38.0681 | 14.0965 | 198.3483 | 22.6088 | 37.8088 | 13.8217 | 195.9655 | 20.4062 | 39.02 | 13.9512 | 195.7643 | 20.8247 | 40.382 | 13.9674 | 197.5507 | 194.2313 | 13.0242 | 53.6878 | 1.84 | 9.9776 | 0 | 77.1629 | 21.3282 | 53.4999 | 13.1969 | 190.5286 | 193.5706 | 12.7843 | 3.1649 | 61.2025 | 6.2802 | 67.4828 | 14.7936 | 131.1475 | 123.7353 | 99.9713 | 14.7719 | 17.7059 | 191.6517 | 121.7065 | 14.7057 | 1.1658 | 37.8275 | 77.9237 | 1.6972 | 0.11026 | 16.5176 | 3.8468 | 0.5758 | 0.36984
2025-06-07 12:00 | 34.0588 | 5.4726 | 0.97018 | 1.0219 | 21.6184 | 2.024 | 12.4277 | 191.9948 | 17.7625 | 191.4895 | 20.1848 | 38.0826 | 14.1894 | 198.5608 | 22.5596 | 38.3089 | 13.9169 | 196.2584 | 20.4442 | 39.3538 | 14.0398 | 196.0918 | 20.8823 | 41.661 | 14.0796 | 197.8655 | 194.3717 | 13.0781 | 54.0864 | 2.011 | 9.9812 | 0 | 77.2891 | 21.3332 | 54.4404 | 13.2465 | 190.6352 | 193.6846 | 12.8265 | 3.3194 | 63.2909 | 5.6436 | 68.9345 | 14.858 | 131.3717 | 124.4837 | 99.9756 | 14.838 | 17.7625 | 191.4895 | 122.7286 | 14.7622 | 1.1184 | 37.884 | 79.3845 | 4.0329 | 0.11155 | 6.9155 | 14.2821 | 0.52095 | 0.37234
2025-06-07 13:00 | 34.4751 | 5.6765 | 0.99641 | 1.0513 | 22.1392 | 2.0067 | 12.6355 | 192.7166 | 17.9877 | 191.3814 | 20.2755 | 37.807 | 14.4365 | 199.3034 | 22.5141 | 38.8689 | 14.1781 | 197.0586 | 20.7825 | 39.7472 | 14.3097 | 197.1007 | 20.8335 | 42.442 | 14.3325 | 198.6148 | 195.1391 | 13.3075 | 55.0484 | 2.195 | 9.9826 | 0 | 77.4104 | 21.3833 | 50.0569 | 13.4257 | 191.1796 | 194.3717 | 13.0263 | 3.7994 | 64.3262 | 4.8547 | 69.1808 | 15.074 | 132.0493 | 125.635 | 99.979 | 15.0548 | 17.9877 | 191.3814 | 123.5445 | 14.9876 | 1.1 | 38.2115 | 80.0215 | 3.9291 | 0.1123 | 0.080246 | 21.1762 | 0.48503 | 0.36988
2025-06-07 14:00 | 34.6273 | 6.2093 | 0.99764 | 1.0504 | 21.9874 | 1.9135 | 12.7257 | 193.058 | 18.0803 | 191.5895 | 20.2993 | 37.307 | 14.5065 | 199.5592 | 22.9762 | 38.9277 | 14.2627 | 197.3577 | 20.5966 | 39.424 | 14.3989 | 197.5817 | 20.5315 | 42.1752 | 14.3795 | 198.6352 | 195.4736 | 13.3982 | 55.1801 | 2.2789 | 9.9806 | 0 | 77.482 | 21.5112 | 48.7571 | 13.5228 | 191.5492 | 194.7044 | 13.1169 | 3.8419 | 61.8203 | 4.4392 | 66.2595 | 15.1962 | 132.0798 | 126.1282 | 99.9776 | 15.1768 | 18.0803 | 191.5895 | 123.4024 | 15.0801 | 1.1355 | 38.211 | 79.6188 | 2.073 | 0.11128 | 0.079337 | 21.8337 | 0.50381 | 0.3667
2025-06-07 15:00 | 34.5713 | 6.4407 | 0.97433 | 1.0283 | 21.4783 | 1.9574 | 12.577 | 192.5423 | 17.9256 | 191.8018 | 20.2259 | 37.0991 | 14.3289 | 199.0206 | 22.8895 | 38.9163 | 14.0756 | 196.7812 | 20.0974 | 38.6007 | 14.2128 | 197.0869 | 20.3592 | 42.0899 | 14.1873 | 197.8767 | 194.9284 | 13.2332 | 54.5502 | 2.0561 | 9.9798 | 0 | 77.5128 | 21.5132 | 53.8415 | 13.4128 | 191.2702 | 194.2434 | 12.9805 | 3.426 | 62.6765 | 4.9935 | 67.67 | 15.0669 | 131.2914 | 125.6917 | 99.9737 | 15.0473 | 17.9256 | 191.8018 | 122.6757 | 14.9252 | 1.1707 | 37.6865 | 79.24 | 2.0464 | 0.11039 | 0.077417 | 21.2335 | 0.53357 | 0.36275
2025-06-07 16:00 | 34.6079 | 6.4428 | 0.94134 | 0.9958 | 20.6484 | 2.0527 | 12.5167 | 192.3246 | 17.8522 | 191.8189 | 20.1828 | 37.1052 | 14.2433 | 198.799 | 22.8419 | 38.9022 | 13.9923 | 196.5126 | 20.1424 | 38.0876 | 14.1418 | 196.7592 | 20.3772 | 42.0755 | 14.1182 | 197.6042 | 194.6723 | 13.1592 | 54.0983 | 1.6306 | 9.9777 | 0 | 77.4605 | 21.319 | 55.2043 | 13.3305 | 190.9734 | 194.0267 | 12.9195 | 3.4712 | 64.9991 | 6.0396 | 71.0387 | 14.9541 | 131.0101 | 124.9637 | 99.9673 | 14.9325 | 17.8522 | 191.8189 | 122.047 | 14.8519 | 1.1934 | 37.5881 | 78.5767 | 3.3456 | 0.11167 | 0.074571 | 19.9977 | 0.57958 | 0.35956
2025-06-07 17:00 | 34.9281 | 7.0281 | 0.92358 | 0.97397 | 19.7854 | 1.9941 | 12.5485 | 192.4408 | 17.8919 | 191.6858 | 20.1758 | 37.1152 | 14.2637 | 198.9433 | 23.0685 | 38.896 | 14.031 | 196.6287 | 20.5605 | 38.0181 | 14.1971 | 196.8743 | 20.3506 | 42.0672 | 14.1638 | 197.7872 | 194.8009 | 13.1944 | 54.4468 | 1.4905 | 9.9733 | 0 | 77.3408 | 21.1999 | 55.2061 | 13.336 | 190.9483 | 194.1234 | 12.9488 | 3.4121 | 63.8943 | 5.7573 | 69.6516 | 14.964 | 131.2703 | 124.4253 | 99.9624 | 14.9398 | 17.8919 | 191.6858 | 121.4614 | 14.8918 | 1.2128 | 37.9107 | 77.3299 | 3.1734 | 0.12009 | 0.072344 | 20.3162 | 0.62435 | 0.36087
2025-06-07 18:00 | 35.0949 | 7.0808 | 0.92275 | 0.96466 | 19.2482 | 1.9636 | 12.598 | 192.6306 | 17.9428 | 191.7546 | 20.1521 | 37.1233 | 14.2874 | 199.0837 | 22.8048 | 38.8988 | 14.0596 | 196.74 | 20.5715 | 38.0227 | 14.2294 | 197.0516 | 20.293 | 42.0731 | 14.1966 | 197.9155 | 194.9987 | 13.2456 | 54.7257 | 1.6437 | 9.9743 | 0 | 77.203 | 21.2069 | 55.2043 | 13.3759 | 191.0681 | 194.3068 | 12.998 | 3.2209 | 63.3643 | 5.5464 | 68.9107 | 14.9919 | 131.7026 | 123.9563 | 99.9604 | 14.9664 | 17.9428 | 191.7546 | 121.2932 | 14.9431 | 1.224 | 38.2561 | 76.4448 | 1.2259 | 0.13018 | 0.071253 | 20.3795 | 0.64436 | 0.36365
2025-06-07 19:00 | 35.0289 | 6.3949 | 0.92015 | 0.95278 | 19.0978 | 1.9572 | 12.5722 | 192.5358 | 17.9128 | 191.8443 | 20.1147 | 37.1272 | 14.2526 | 198.9825 | 23.1521 | 38.9029 | 14.0301 | 196.6718 | 20.2139 | 38.0237 | 14.1831 | 196.9169 | 20.279 | 42.0742 | 14.1637 | 197.7923 | 194.8914 | 13.2149 | 54.6127 | 1.8636 | 9.9724 | 0 | 77.0702 | 21.2168 | 55.2083 | 13.3496 | 190.9701 | 194.2146 | 12.972 | 3.1325 | 62.7854 | 5.7727 | 68.558 | 14.9637 | 131.6987 | 123.9577 | 99.9599 | 14.9383 | 17.9128 | 191.8443 | 121.1114 | 14.913 | 1.2293 | 38.1962 | 76.1852 | 1.479 | 0.13285 | 0.070941 | 20.31 | 0.64793 | 0.36438
2025-06-07 20:00 | 34.9483 | 6.096 | 0.91248 | 0.93957 | 19.0589 | 1.9562 | 12.5642 | 192.4973 | 17.9014 | 191.8715 | 20.0942 | 37.1288 | 14.2474 | 198.9543 | 23.2371 | 38.9026 | 14.0253 | 196.6559 | 20.3103 | 38.0238 | 14.1816 | 196.8311 | 20.2833 | 42.0753 | 14.1613 | 197.775 | 194.8436 | 13.2048 | 54.3907 | 2.0553 | 9.9649 | 0 | 76.9345 | 21.2103 | 55.0818 | 13.3406 | 190.9117 | 194.1765 | 12.9636 | 3.1455 | 62.3581 | 6.0079 | 68.3661 | 14.9467 | 131.7701 | 123.7787 | 99.9605 | 14.9212 | 17.9014 | 191.8715 | 121.2328 | 14.9013 | 1.2337 | 38.2551 | 76.1713 | 2.3956 | 0.13213 | 0.070747 | 20.1698 | 0.65138 | 0.36499
2025-06-07 21:00 | 34.8406 | 5.5482 | 0.91011 | 0.94165 | 19.1069 | 1.9537 | 12.3908 | 191.9131 | 17.7455 | 191.798 | 20.0238 | 37.1292 | 14.0838 | 198.4526 | 23.072 | 38.9006 | 13.857 | 196.1518 | 20.6524 | 38.0244 | 14.0289 | 196.3824 | 20.2439 | 40.1362 | 13.9766 | 197.4698 | 194.3149 | 13.0412 | 54.6165 | 2.1811 | 9.9632 | 0 | 76.8069 | 21.1954 | 55.085 | 13.1828 | 190.462 | 193.621 | 12.7967 | 3.2806 | 62.6499 | 5.4184 | 68.0683 | 14.8229 | 130.9802 | 123.9706 | 99.9611 | 14.7978 | 17.7455 | 191.798 | 121.3986 | 14.7456 | 1.2347 | 37.7392 | 76.8371 | 1.4709 | 0.13189 | 0.070609 | 20.5818 | 0.65421 | 0.36612
2025-06-07 22:00 | 34.6356 | 5.5424 | 0.90692 | 0.94446 | 19.2724 | 1.9787 | 12.1437 | 191.0622 | 17.5109 | 191.1949 | 19.9283 | 37.1302 | 13.8372 | 197.6863 | 22.8732 | 38.9008 | 13.6048 | 195.336 | 20.5728 | 38.0252 | 13.7756 | 195.662 | 20.2242 | 38.1316 | 13.7063 | 196.777 | 193.4969 | 12.7941 | 54.5633 | 2.2836 | 9.9665 | 0 | 76.701 | 21.1693 | 55.2099 | 12.9555 | 189.7693 | 192.8091 | 12.5567 | 3.2867 | 62.7842 | 5.7507 | 68.5348 | 14.6338 | 129.7176 | 124.1273 | 99.9602 | 14.6095 | 17.5109 | 191.1949 | 121.1748 | 14.511 | 1.2341 | 36.9483 | 77.6441 | 0.66482 | 0.13151 | 0.070672 | 20.8075 | 0.65361 | 0.36607
2025-06-07 23:00 | 34.394 | 5.5559 | 0.88324 | 0.92142 | 19.0176 | 2.0159 | 12.1562 | 191.0802 | 17.4962 | 190.854 | 20.0625 | 36.7167 | 13.8202 | 197.6147 | 22.6856 | 38.9027 | 13.5898 | 195.2373 | 20.2425 | 38.0263 | 13.7498 | 195.5683 | 20.499 | 38.0661 | 13.6994 | 196.6237 | 193.4522 | 12.7888 | 53.8434 | 2.4015 | 9.9658 | 0 | 76.6036 | 21.1406 | 51.7018 | 12.9509 | 189.6752 | 192.8057 | 12.5616 | 3.2138 | 61.9486 | 7.388 | 69.3366 | 14.6104 | 129.7025 | 123.9116 | 99.9602 | 14.5859 | 17.4962 | 190.854 | 121.1235 | 14.4963 | 1.2341 | 37.0685 | 77.7382 | 1.1984 | 0.13124 | 0.070669 | 19.1984 | 0.65233 | 0.36521
2025-06-08 | 33.9116 | 6.786 | 0.88887 | 0.92462 | 18.901 | 1.937 | 12.166 | 191.1496 | 17.4916 | 190.8265 | 20.2285 | 36.0877 | 13.7787 | 197.5494 | 20.9425 | 38.9036 | 13.5289 | 195.1254 | 20.138 | 38.0291 | 13.7045 | 195.4493 | 20.8762 | 38.073 | 13.6716 | 196.6711 | 193.4927 | 12.7898 | 53.8962 | 2.4783 | 9.9605 | 0 | 76.5079 | 21.1495 | 46.2765 | 12.9354 | 189.6878 | 192.8211 | 12.557 | 3.2446 | 60.2414 | 5.4461 | 65.6875 | 14.7214 | 130.8836 | 124.3468 | 99.9631 | 14.6962 | 17.4916 | 190.8265 | 121.3786 | 14.6178 | 8.0392 | 31.9705 | 77.5442 | 6.568 | 0.13659 | 0.070679 | 33.446 | 6.5821 | 3.1978
Total | MW: 829.4335; MVAR: 142.2857; kg/s: 4664629.9267; kg/s: 285188.4033; kg/s: 5314241.2928; kg/s: 552461.2933; kg/s: 5866702.586; kg/s: 11330197.8707
Average | 34.5597 | 5.9286 | 0.91204 | 0.95356 | 19.5268 | 1.965 | 12.4416 | 192.0792 | 17.7716 | 191.6648 | 20.1792 | 37.3411 | 14.129 | 198.5398 | 22.604 | 38.3625 | 13.8806 | 196.1762 | 20.5262 | 38.1724 | 14.0334 | 196.25 | 20.6671 | 40.5683 | 14.0262 | 197.6201 | 194.4251 | 13.0787 | 53.9888 | 1.8744 | 9.973 | 0 | 77.0836 | 21.3113 | 53.2157 | 13.235 | 190.6164 | 193.7652 | 12.841 | 3.3008 | 61.5074 | 6.3942 | 67.9017 | 14.8603 | 131.1365 | 124.2548 | 99.9644 | 14.8364 | 17.7716 | 191.6648 | 121.5936 | 14.7769 | 1.5015 | 37.5296 | 77.4934 | 2.2303 | 0.12797 | 8.6146 | 11.6021 | 0.8608 | 0.48737
Min | 33.9116 | 3.5849 | 0.86869 | 0.89758 | 17.9135 | 1.8588 | 12.1437 | 191.0622 | 17.4916 | 190.8265 | 19.9283 | 36.0877 | 13.7787 | 197.5494 | 20.9425 | 37.7623 | 13.5289 | 195.1254 | 20.0974 | 36.0446 | 13.7045 | 195.4493 | 20.2242 | 38.0661 | 13.6716 | 196.6237 | 193.4522 | 12.7888 | 52.5623 | 1.4905 | 9.9605 | 0 | 76.5079 | 21.1406 | 46.2765 | 12.9354 | 189.6752 | 192.8057 | 12.5567 | 3.1325 | 58.3595 | 4.4392 | 64.5574 | 14.6104 | 129.7025 | 123.5592 | 99.9558 | 14.5859 | 17.4916 | 190.8265 | 120.8103 | 14.4963 | 1.1 | 31.9705 | 76.1713 | 0.1067 | 0.11026 | 0.070609 | 0.084601 | 0.48503 | 0.35956
Max | 35.0949 | 7.3029 | 0.99764 | 1.0513 | 22.1392 | 2.0527 | 12.7257 | 193.058 | 18.0803 | 192.0833 | 20.324 | 38.0826 | 14.5065 | 199.5592 | 23.2371 | 38.9277 | 14.2627 | 197.3577 | 21.143 | 39.7472 | 14.3989 | 197.5817 | 21.1499 | 42.442 | 14.3795 | 198.6352 | 195.4736 | 13.3982 | 55.1801 | 2.4783 | 9.9826 | 0 | 77.5128 | 21.5687 | 55.2099 | 13.5228 | 191.5492 | 194.7044 | 13.1169 | 3.8419 | 64.9991 | 9.0833 | 71.0387 | 15.1962 | 132.0798 | 126.1282 | 99.979 | 15.1768 | 18.0803 | 192.0833 | 123.5445 | 15.0801 | 8.0392 | 38.2561 | 80.0215 | 6.568 | 0.15249 | 19.4116 | 33.446 | 6.5821 | 3.1978

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day
16 |  | Night
17 | 2025-06-09 | Day
18 |  | Night
19 | 2025-06-10 | Day
20 |  | Night
21 | 2025-06-11 | Day
22 |  | Night
23 | 2025-06-12 | Day
24 |  | Night
25 | 2025-06-13 | Day
26 |  | Night
27 | 2025-06-14 | Day
28 |  | Night
29 | 2025-06-15 | Day
30 |  | Night
31 | 2025-06-16 | Day
32 |  | Night
33 | 2025-06-17 | Day
34 |  | Night
35 | 2025-06-18 | Day
36 |  | Night
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-07
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0