## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-08
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 19.9309 | 198.1616 | 37.8101
|  | #6-2 | Production | 22.1775 | 195.7591 | 37.8959
|  | #6-3 | Production | 20.3203 | 196.1962 | 38.2625
|  | #6-4 | Production | 20.3376 | 197.1909 | 41.3699
|  | #8-1 | Shut in | 2.8751 | 75.8484 | 9.9736
|  | #8-2 | Production | 21.2858 | 190.1706 | 52.6633
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 53.9256 | 4659169.913
|  | PAD #8 - STEAM |  |  |  |  | 3.3097 | 285954.584 | Online
|  | BRINE HEADER |  |  |  |  | 6.4027 | 553190.0623 | Offline
|  | TOTAL FLOW |  |  |  |  | 63.6379 | 5498314.5594
|  | PRESS SEPARATOR IJN 6 | Online | 12.9645 | 194.0342
|  | PRESS SEPARATOR IJN 8 | Online | 12.7256 | 193.361
| INJECTION WELL | #5-1 | Injection | 14.7269 | 124.0788 | 99.9625 | 130.6784 | 11290617.2488
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.4841 |  |  | 827.6191
|  | NET | 31.7849 |  |  | 762.8375
| PARASITIC LOAD |  | 2.6992 |  |  | 64.7816
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 1.8454 |  |  | 6643.5328
|  | NET | 2.0021 |  |  | 7207.7144
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
8. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 9. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
10. DHP tools pull out at Well IJN 9-1 and Well IJN8-1 was done by Toptek. Master valve and crown valve closed
11. Brine Dump Control valve Ijen-6 PV-2227A indication passing

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-08
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 762837.4629 |  |  |  | 762837.4629
|  |  |  | 762837.4629 |  | 0 |  | 762837.4629
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 763180 | [7 empty] | 763180
M-T-D GROSS GENERATION (kWHR) |  |  |  | 6612471 | [7 empty] | 6612471
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18306.5 | 0 | 6415.81 | 43.6 | 1041 | 1604 | 27410.91
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 146928.8 | -283254.3 | 48260.11 | 349.5 | 10763 | 12974 | 72346.61
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.4841 |  |  | 6.2548 |  | 19.2446
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 192
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 92.14%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 4659.1699 |  | 285.9546 |  |  | 5215.6034
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.053926 |  | 0.0033097 |  |  | 0.060366
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 553.1901
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.0064027
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 5768.7934
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.066768
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 191.6627 |  |  |  | 191.0978
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.3244 |  |  |  | 17.6571
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 17.3305 |  | 21.5962 |  |  | 19.2446
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:02 | PLN adviced load ROH 31.72 MW (Mr. Imam Samsudin)
2:55 | Start pit pump IJN 8 (Level pond : 32.5%)
5:47 | Stop pit pump IJN 8 (Level pond : 27.9%)
6:45 | Inspection Cubicle 110VDC, Cubicle 220VDC and Cubicle 48VDC in 150kV room - done. Result Ok, no alarm
7:05 | Inspection Cubicle 110VDC in electric room - done. Result OK and no alarm
7:55 | Handover shift and toolbox meeting
9:21 | Test run of Pit Pump IJN 6 - Engine (P2203B) but have problem trip while speed up 900rpm [standard activities schedule]
9:34 | Test run of Pit Pump IJN 6 - Electric (P2203A) with pressure discharge 18.5bar [standard activities schedule]
10:05 | Stop Electrical pit pump IJN 6 (Level pond : 19.3%)
10:37 | Drain Suction Strainer-A Booster Pump IJN 6 [standard activities schedule]
10:46 | Test run of Pit Pump IJN 8 - Electric (P2303) with pressure discharge 21.8bar [standard activities schedule]
11:13 | Drain Suction Strainer-A Booster Pump IJN 8 [standard activities schedule]
13:30 | Inspection of Switchgears [standard activities schedule]
14:46 | Stop pit pump IJN 8 (Level pond : 27.7%)
15:00 | Drain Brine Manifold Strainer-A SP2501 inlet preheater [standard activities schedule]
15:30 | Check the clogged drain valve on the discharge Brine Booster Pump B IJN8
17:55 | Start pit pump IJN 8 (Level pond : 32.0%)
20:48 | Stop pit pump IJN 8 (Level pond : 26.8%)
20:49 | Start electrical pit pump IJN 6 (Level pond : 24.9%)
21:00 | PLN adviced load ROH 31.72 MW (Mr. M Bahrul alam)
22:02 | PLN adviced load ROH 31.72 MW (Mr. Inggih Surya)
23:55 | Stop electrical pit pump IJN 6 (Level pond : 19.0%)
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Tio |  |  |  | Steamfield : Dede
Night Shift | Shift Leader : Zakariya |  |  |  | CCR Operator : Ois |  |  |  | Steamfield : Dadan
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-08
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2181710 | 2182760 | 1050 | 54910
(BACKUP) |  | 2126290 | 2180090 | 2181130 | 1040 | 54840
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 98414750 | 99177930 | 763180 | 6076020
(BACKUP) |  | 93082960 | 98394300 | 99157260 | 762960 | 6074300
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4339500 | 4376430 | 36930 | 234200
(BACKUP) |  | 4144060 | 4341400 | 4378350 | 36950 | 234290
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 107105995 | 107935726 | 829731 | 6612471
TOTAL |  |  |  |  | 829731 | 6612471
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 17458143 | 17607996 | 149853 | 1077741
TOTAL |  |  |  |  | 149853 | 1077741
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3217940.64 | 3236247.14 | 18306.5 | 146928.8
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1031602.71 | 1038018.52 | 6415.81 | 48260.11
U Ijen 5 |  | 7258.6 | 7564.5 | 7608.1 | 43.6 | 349.5
U Ijen 6 |  | 247889 | 257611 | 258652 | 1041 | 10763
U Ijen 8 |  | 299837 | 311207 | 312811 | 1604 | 12974
TOTAL |  |  |  |  | 27410.91 | 219275.41
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-08 01:00 | 34.4034 | 5.895 | 0.90403 | 0.93763 | 19.0963 | 1.992 | 12.3405 | 191.7208 | 17.6747 | 191.2071 | 20.0249 | 37.9679 | 14.0188 | 198.2339 | 22.5164 | 38.9022 | 13.7841 | 195.8824 | 20.417 | 38.0259 | 13.9517 | 196.1409 | 20.8481 | 39.5032 | 13.9169 | 197.0278 | 194.0782 | 12.9762 | 53.8803 | 2.4865 | 9.9671 | 0 | 76.4324 | 21.2718 | 50.1294 | 13.1121 | 190.1454 | 193.3996 | 12.7364 | 3.0494 | 61.8225 | 6.7106 | 68.5331 | 14.7585 | 130.754 | 124.0271 | 99.9603 | 14.7333 | 17.6747 | 191.2071 | 121.6383 | 14.6745 | 1.4129 | 37.5567 | 77.7123 | 2.3633 | 0.12938 | 0.15661 | 19.9838 | 0.88826 | 0.46898
2025-06-08 02:00 | 34.6453 | 5.2762 | 0.89876 | 0.93918 | 19.0021 | 1.972 | 12.3186 | 191.6507 | 17.6674 | 191.2947 | 19.9755 | 38.0993 | 14.0099 | 198.2061 | 22.4858 | 38.9019 | 13.7736 | 195.8672 | 20.392 | 38.0244 | 13.9396 | 196.0884 | 20.7875 | 40.0609 | 13.9073 | 196.9403 | 194.0387 | 12.9623 | 54.3099 | 2.5642 | 9.9745 | 0 | 76.3627 | 21.3355 | 50.2394 | 13.0991 | 190.1253 | 193.345 | 12.7185 | 3.1882 | 62.2654 | 6.0568 | 68.3221 | 14.7615 | 130.5502 | 124.2762 | 99.9602 | 14.7366 | 17.6674 | 191.2947 | 121.3981 | 14.6676 | 1.3265 | 37.5293 | 77.4194 | 2.0387 | 0.12795 | 0.070997 | 20.5865 | 0.8125 | 0.38679
2025-06-08 03:00 | 34.5317 | 4.774 | 0.89666 | 0.93684 | 19.0364 | 1.9912 | 12.2286 | 191.3393 | 17.575 | 191.1801 | 19.9321 | 38.0981 | 13.92 | 197.9172 | 22.3197 | 38.9014 | 13.6788 | 195.5442 | 20.2674 | 38.0234 | 13.8436 | 195.7288 | 20.6377 | 40.0606 | 13.8086 | 196.5635 | 193.7337 | 12.8707 | 54.0912 | 2.6587 | 9.9757 | 0 | 76.2738 | 21.3523 | 50.2411 | 13.0163 | 189.8746 | 193.0484 | 12.6307 | 3.2829 | 62.2228 | 6.5379 | 68.7607 | 14.6811 | 130.1771 | 123.9494 | 99.96 | 14.6564 | 17.575 | 191.1801 | 121.2778 | 14.5752 | 1.3307 | 37.3606 | 77.3526 | 1.9699 | 0.12685 | 0.070953 | 19.9463 | 0.81223 | 0.38519
2025-06-08 04:00 | 34.5243 | 5.2839 | 0.90518 | 0.93689 | 19.1529 | 1.9869 | 12.2527 | 191.4202 | 17.5992 | 190.9759 | 19.9122 | 38.0978 | 13.9423 | 197.9887 | 22.5698 | 38.9012 | 13.7057 | 195.5952 | 20.3504 | 38.0267 | 13.8695 | 195.8088 | 20.5976 | 40.06 | 13.8343 | 196.7388 | 193.8089 | 12.8944 | 54.103 | 2.6708 | 9.9676 | 0 | 76.1611 | 21.3531 | 50.2434 | 13.0368 | 189.9179 | 193.1242 | 12.6544 | 3.2464 | 62.2416 | 6.3544 | 68.596 | 14.6978 | 130.2968 | 123.9575 | 99.9601 | 14.6729 | 17.5992 | 190.9759 | 121.3418 | 14.5994 | 1.3407 | 37.5002 | 77.3171 | 1.9307 | 0.12715 | 0.070643 | 20.0925 | 0.8154 | 0.38499
2025-06-08 05:00 | 34.6282 | 6.1783 | 0.90105 | 0.9306 | 19.0364 | 1.9723 | 12.2693 | 191.4699 | 17.6237 | 191.0075 | 19.9225 | 38.0991 | 13.9642 | 198.0517 | 22.6555 | 38.9019 | 13.7294 | 195.6937 | 20.4371 | 38.0297 | 13.8925 | 195.8946 | 20.6275 | 40.0599 | 13.8605 | 196.9894 | 193.8706 | 12.9154 | 54.338 | 2.7322 | 9.9616 | 0 | 76.0534 | 21.3592 | 50.2428 | 13.0525 | 189.9313 | 193.1741 | 12.6717 | 3.1408 | 62.3666 | 5.9302 | 68.2968 | 14.7173 | 130.384 | 124.1072 | 99.9606 | 14.6925 | 17.6237 | 191.0075 | 121.3471 | 14.6239 | 1.3458 | 37.5441 | 77.3544 | 1.6998 | 0.12653 | 0.070517 | 20.5924 | 0.81873 | 0.38549
2025-06-08 06:00 | 34.6035 | 5.8756 | 0.88696 | 0.92464 | 19.0674 | 1.9823 | 12.2325 | 191.3423 | 17.5803 | 191.0744 | 19.923 | 38.0989 | 13.9234 | 197.9172 | 22.2431 | 38.9014 | 13.681 | 195.556 | 20.3403 | 38.0303 | 13.8433 | 195.7371 | 20.643 | 40.0609 | 13.8161 | 196.817 | 193.7403 | 12.8765 | 54.3128 | 2.9007 | 9.9683 | 0 | 75.9683 | 21.3649 | 50.2461 | 13.0198 | 189.8307 | 193.0486 | 12.6349 | 3.3346 | 62.2328 | 6.3631 | 68.5959 | 14.6808 | 130.2938 | 123.9931 | 99.9614 | 14.6561 | 17.5803 | 191.0744 | 121.2298 | 14.5804 | 1.3419 | 37.4408 | 77.2821 | 1.5733 | 0.12469 | 0.07074 | 20.1088 | 0.81529 | 0.38506
2025-06-08 07:00 | 34.4788 | 6.0682 | 0.88753 | 0.93163 | 19.3975 | 1.9971 | 12.2133 | 191.2921 | 17.5516 | 191.0146 | 19.9109 | 38.098 | 13.9021 | 197.8416 | 22.0733 | 38.8986 | 13.6525 | 195.4693 | 20.2486 | 38.0368 | 13.811 | 195.6403 | 20.6392 | 40.0604 | 13.7878 | 196.6965 | 193.6764 | 12.8532 | 54.1429 | 3.0408 | 9.9745 | 0 | 75.9374 | 21.3721 | 50.2495 | 13.0054 | 189.8214 | 192.9946 | 12.6155 | 3.4809 | 62.0404 | 6.8179 | 68.8583 | 14.6559 | 130.3498 | 123.8655 | 99.9623 | 14.6316 | 17.5516 | 191.0146 | 121.1145 | 14.5515 | 1.3227 | 37.4535 | 77.1862 | 1.5664 | 0.1212 | 0.07141 | 19.7002 | 0.8079 | 0.38591
2025-06-08 08:00 | 34.3242 | 6.7287 | 0.9049 | 0.95058 | 19.7355 | 1.9948 | 12.237 | 191.3674 | 17.5731 | 191.0089 | 19.9146 | 38.0981 | 13.9344 | 197.9101 | 22.1531 | 38.7127 | 13.6824 | 195.5415 | 20.3278 | 38.2255 | 13.8393 | 195.7396 | 20.6188 | 40.2459 | 13.8167 | 196.7446 | 193.7428 | 12.8766 | 53.9352 | 3.1485 | 9.9727 | 0 | 75.9535 | 21.3861 | 50.4232 | 13.0324 | 189.8913 | 193.0616 | 12.6383 | 3.599 | 61.7051 | 6.7656 | 68.4707 | 14.6715 | 130.5653 | 123.902 | 99.9643 | 14.6478 | 17.5731 | 191.0089 | 121.4889 | 14.573 | 1.2926 | 37.6256 | 77.6578 | 2.2123 | 0.1156 | 0.072463 | 19.4874 | 0.79219 | 0.3859
2025-06-08 09:00 | 34.4389 | 6.9006 | 0.92911 | 0.97822 | 20.3044 | 1.7914 | 12.3372 | 191.6993 | 17.6849 | 190.909 | 19.9421 | 38.0985 | 14.0657 | 198.2951 | 22.2434 | 37.7744 | 13.8179 | 195.9678 | 20.5703 | 39.2155 | 13.9886 | 196.2647 | 20.6489 | 41.2525 | 13.9684 | 197.1709 | 194.097 | 12.9898 | 54.3282 | 3.2164 | 9.9741 | 0 | 76.0104 | 21.4068 | 51.3796 | 13.135 | 190.1921 | 193.3843 | 12.7386 | 3.4176 | 56.1053 | 5.5874 | 61.6928 | 14.7706 | 130.9272 | 124.201 | 99.9654 | 14.747 | 17.6849 | 190.909 | 122.0548 | 14.6847 | 1.2539 | 37.8825 | 78.1339 | 3.7108 | 0.11123 | 0.074306 | 20.3962 | 0.75817 | 0.37836
2025-06-08 10:00 | 34.6835 | 6.9864 | 0.95532 | 1.0066 | 20.8329 | 1.6484 | 12.383 | 191.8669 | 17.7492 | 190.7548 | 19.9859 | 38.0997 | 14.15 | 198.5096 | 22.0663 | 36.9882 | 13.8919 | 196.1736 | 20.5106 | 40.0228 | 14.0758 | 196.6176 | 20.6435 | 42.0829 | 14.0497 | 197.5345 | 194.3187 | 13.0546 | 54.9171 | 3.2645 | 9.9796 | 0 | 76.1216 | 21.4333 | 52.1739 | 13.1898 | 190.4075 | 193.558 | 12.7857 | 3.176 | 52.608 | 4.5644 | 57.1724 | 14.8468 | 130.9201 | 124.6898 | 99.9671 | 14.8243 | 17.7492 | 190.7548 | 122.4151 | 14.7493 | 1.2157 | 37.8759 | 78.5604 | 2.9068 | 0.1104 | 0.076589 | 21.6681 | 0.7135 | 0.36429
2025-06-08 11:00 | 34.4165 | 6.8233 | 0.97779 | 1.0309 | 21.317 | 1.5965 | 12.3778 | 191.8547 | 17.7353 | 190.8875 | 19.9974 | 38.1012 | 14.1348 | 198.4224 | 22.0192 | 36.6052 | 13.8662 | 196.0369 | 20.0732 | 39.702 | 14.0256 | 196.4826 | 20.4524 | 42.099 | 14.0058 | 197.5117 | 194.2958 | 13.0441 | 54.6805 | 3.2695 | 9.9833 | 0 | 76.2314 | 21.443 | 53.3351 | 13.1967 | 190.4722 | 193.5541 | 12.78 | 3.2557 | 50.3031 | 4.6431 | 54.9461 | 14.8539 | 130.6306 | 125.0592 | 99.9703 | 14.8329 | 17.7353 | 190.8875 | 122.7752 | 14.7359 | 1.1864 | 37.7252 | 79.4562 | 1.0685 | 0.11103 | 0.078471 | 21.1412 | 0.67465 | 0.35632
2025-06-08 12:00 | 34.0527 | 6.4525 | 0.97579 | 1.0306 | 21.5962 | 1.6906 | 12.2851 | 191.5206 | 17.6332 | 191.1055 | 19.9767 | 38.1016 | 14.0273 | 198.0714 | 22.0842 | 36.639 | 13.7573 | 195.6735 | 19.8409 | 38.6892 | 13.8851 | 195.9827 | 20.3045 | 42.1048 | 13.8875 | 197.0665 | 193.9369 | 12.9389 | 54.2435 | 3.2657 | 9.9835 | 0 | 76.2927 | 21.4024 | 54.8401 | 13.1149 | 190.2475 | 193.245 | 12.6898 | 3.4642 | 52.1078 | 5.4611 | 57.5689 | 14.7794 | 130.0296 | 125.1904 | 99.9722 | 14.7596 | 17.6332 | 191.1055 | 122.669 | 14.6339 | 1.1789 | 37.2747 | 80.0078 | 1.2888 | 0.11112 | 0.078386 | 20.6054 | 0.66271 | 0.35158
2025-06-08 13:00 | 34.1403 | 6.7032 | 0.95253 | 1.0008 | 20.841 | 1.9404 | 12.1814 | 191.1355 | 17.5367 | 190.9647 | 19.9429 | 38.1003 | 13.928 | 197.7719 | 22.1251 | 37.0191 | 13.6641 | 195.3757 | 19.9174 | 38.0014 | 13.798 | 195.6225 | 20.3046 | 42.4827 | 13.8137 | 196.8195 | 193.5612 | 12.8343 | 54.1789 | 3.313 | 9.9783 | 0 | 76.2558 | 21.303 | 55.2091 | 13.0076 | 189.8953 | 192.8812 | 12.5898 | 3.5203 | 60.1885 | 6.0586 | 66.2471 | 14.6872 | 129.6992 | 124.904 | 99.9703 | 14.6669 | 17.5367 | 190.9647 | 122.1036 | 14.5369 | 1.2117 | 37.0036 | 79.539 | 2.9331 | 0.1104 | 0.07603 | 20.364 | 0.69639 | 0.34511
2025-06-08 14:00 | 34.4745 | 6.9235 | 0.94211 | 0.98629 | 19.9623 | 1.9753 | 12.2364 | 191.3295 | 17.6013 | 190.7138 | 19.9374 | 38.098 | 13.9873 | 197.999 | 22.0556 | 37.0138 | 13.7303 | 195.5978 | 20.3596 | 38.0059 | 13.8972 | 195.9764 | 20.3341 | 42.9609 | 13.9063 | 197.2564 | 193.7731 | 12.8962 | 54.5563 | 3.4041 | 9.9757 | 0 | 76.1483 | 21.2245 | 55.2092 | 13.0502 | 189.9961 | 193.0645 | 12.6451 | 3.4163 | 62.722 | 5.3762 | 68.0982 | 14.7206 | 130.2452 | 124.4797 | 99.9675 | 14.6993 | 17.6013 | 190.7138 | 121.9286 | 14.6009 | 1.2392 | 37.424 | 78.8221 | 3.4185 | 0.11041 | 0.074377 | 20.8032 | 0.73024 | 0.34306
2025-06-08 15:00 | 34.6477 | 6.6572 | 0.94158 | 0.98434 | 19.5961 | 1.966 | 12.2563 | 191.4198 | 17.6266 | 190.624 | 19.9319 | 38.0971 | 14.0027 | 198.0609 | 21.9059 | 37.0155 | 13.7438 | 195.65 | 20.5081 | 38.0108 | 13.9224 | 196.2851 | 20.161 | 43.0604 | 13.919 | 197.4144 | 193.8779 | 12.9205 | 54.8201 | 3.5198 | 9.9764 | 0 | 76.0429 | 21.2095 | 55.2025 | 13.0692 | 190.0728 | 193.1482 | 12.6642 | 3.3982 | 63.0836 | 5.0352 | 68.1187 | 14.7451 | 130.2599 | 124.4613 | 99.9656 | 14.7238 | 17.6266 | 190.624 | 121.9873 | 14.6262 | 1.2504 | 37.5004 | 78.5706 | 1.7717 | 0.11067 | 0.073891 | 21.4696 | 0.73432 | 0.3437
2025-06-08 16:00 | 34.5493 | 6.4785 | 0.92201 | 0.96324 | 19.3421 | 1.9858 | 12.2266 | 191.3227 | 17.5862 | 190.7645 | 19.8794 | 38.0997 | 13.935 | 197.8958 | 21.8704 | 37.1447 | 13.6834 | 195.4445 | 20.112 | 38.0138 | 13.8505 | 196.1776 | 19.9349 | 43.0642 | 13.8536 | 197.2076 | 193.7468 | 12.8781 | 54.4803 | 2.3335 | 9.9741 | 0 | 75.9331 | 21.1958 | 55.2012 | 13.0338 | 189.9569 | 193.0487 | 12.6331 | 3.2292 | 62.8329 | 5.7739 | 68.6068 | 14.7119 | 129.9429 | 124.5528 | 99.9629 | 14.689 | 17.5862 | 190.7645 | 121.7904 | 14.5857 | 1.2656 | 37.3 | 78.3798 | 1.1011 | 0.11568 | 0.072825 | 20.7824 | 0.74974 | 0.34387
2025-06-08 17:00 | 34.4562 | 7.0475 | 0.90895 | 0.94803 | 19.0906 | 2.0011 | 12.2375 | 191.345 | 17.5875 | 190.8822 | 19.8416 | 38.1029 | 13.9297 | 197.9175 | 22.1326 | 37.5398 | 13.6919 | 195.4656 | 20.1874 | 38.0119 | 13.8629 | 196.0893 | 19.911 | 43.0696 | 13.8657 | 197.2081 | 193.7423 | 12.8803 | 54.0779 | 1.2626 | 9.9727 | 0 | 75.7982 | 21.1714 | 55.206 | 13.0341 | 189.9021 | 193.0716 | 12.643 | 3.288 | 62.7467 | 6.2052 | 68.9519 | 14.6961 | 130.1476 | 124.1874 | 99.9611 | 14.672 | 17.5875 | 190.8822 | 121.5462 | 14.5868 | 1.2803 | 37.4612 | 77.8139 | 2.7284 | 0.12592 | 0.07142 | 20.0182 | 0.7823 | 0.34565
2025-06-08 18:00 | 34.7313 | 6.3303 | 0.89195 | 0.92747 | 18.6519 | 1.9771 | 12.3579 | 191.7381 | 17.7 | 190.8315 | 19.8511 | 37.8885 | 14.0388 | 198.2684 | 22.1503 | 37.811 | 13.8078 | 195.7793 | 20.6499 | 38.0143 | 13.9936 | 196.4713 | 19.9351 | 42.8586 | 13.9815 | 197.5555 | 194.1281 | 13.0022 | 53.7353 | 2.0118 | 9.9723 | 0 | 75.6146 | 21.1607 | 54.5638 | 13.1423 | 190.1476 | 193.4511 | 12.7611 | 3.4713 | 62.3088 | 6.3584 | 68.6672 | 14.7744 | 130.9 | 123.9308 | 99.9595 | 14.7493 | 17.7 | 190.8315 | 121.4278 | 14.6998 | 1.2941 | 37.9979 | 77.0482 | 2.6554 | 0.13426 | 0.070507 | 19.8686 | 0.80276 | 0.34726
2025-06-08 19:00 | 34.7546 | 4.5381 | 0.85678 | 0.8924 | 18.2536 | 1.954 | 12.5393 | 192.4055 | 17.8263 | 191.0853 | 19.9079 | 37.3845 | 14.1659 | 198.6986 | 22.0393 | 37.8191 | 13.9347 | 196.1984 | 20.4999 | 38.0209 | 14.108 | 196.9684 | 19.8969 | 42.1125 | 14.0906 | 197.9316 | 194.7149 | 13.1663 | 53.2103 | 2.9953 | 9.9712 | 0 | 75.4146 | 21.1832 | 53.0048 | 13.2994 | 190.6716 | 194.0575 | 12.9306 | 3.2449 | 60.7336 | 7.1752 | 67.9088 | 14.8813 | 131.5241 | 124.1803 | 99.959 | 14.8557 | 17.8263 | 191.0853 | 121.4043 | 14.8268 | 1.2984 | 38.4209 | 76.3279 | 0.7404 | 0.1362 | 0.07026 | 18.0146 | 0.80598 | 0.34632
2025-06-08 20:00 | 34.2717 | 4.8368 | 0.84614 | 0.88789 | 18.1199 | 2.0059 | 12.4896 | 192.2681 | 17.7393 | 191.6848 | 19.8903 | 37.2295 | 14.0834 | 198.4527 | 22.0195 | 37.8232 | 13.8485 | 195.9989 | 20.0704 | 38.0283 | 14.0077 | 196.6284 | 19.8538 | 41.0917 | 13.9861 | 197.569 | 194.5021 | 13.0932 | 52.4585 | 3.5417 | 9.9702 | 0 | 75.2695 | 21.2424 | 52.9638 | 13.2536 | 190.6083 | 193.9012 | 12.8765 | 3.0497 | 60.3142 | 8.4302 | 68.7444 | 14.8138 | 131.0094 | 124.0613 | 99.9584 | 14.7886 | 17.7393 | 191.6848 | 120.6579 | 14.7397 | 1.2947 | 38.1255 | 75.4809 | 0.31739 | 0.13865 | 0.070268 | 16.5422 | 0.80625 | 0.34694
2025-06-08 21:00 | 34.4111 | 6.1053 | 0.86843 | 0.91081 | 17.8724 | 2.0005 | 12.4346 | 192.0527 | 17.7265 | 191.7354 | 19.8333 | 37.6976 | 14.0623 | 198.379 | 22.0585 | 37.821 | 13.8295 | 195.9322 | 20.407 | 38.0339 | 14.009 | 196.5168 | 20.0521 | 41.816 | 13.9874 | 197.4396 | 194.3213 | 13.0474 | 52.8586 | 3.4688 | 9.9706 | 0 | 75.1699 | 21.2679 | 54.5357 | 13.2257 | 190.4835 | 193.7339 | 12.8328 | 3.1487 | 61.6125 | 7.2275 | 68.8399 | 14.7851 | 131.3317 | 123.3731 | 99.9566 | 14.7595 | 17.7265 | 191.7354 | 120.4495 | 14.7268 | 1.2898 | 38.3773 | 75.0732 | 2.343 | 0.14608 | 0.070061 | 17.9185 | 0.80221 | 0.34768
2025-06-08 22:00 | 34.8787 | 6.7765 | 0.87888 | 0.91838 | 17.5143 | 1.9489 | 12.5183 | 192.3527 | 17.8307 | 191.5721 | 19.8998 | 37.2653 | 14.1533 | 198.6833 | 22.1403 | 37.8193 | 13.9293 | 196.264 | 20.7617 | 38.0349 | 14.1202 | 196.9647 | 20.2443 | 42.0729 | 14.0917 | 197.8755 | 194.6619 | 13.1457 | 53.4889 | 2.9685 | 9.9714 | 0 | 75.0781 | 21.1948 | 54.1584 | 13.3092 | 190.7536 | 194.0394 | 12.9195 | 3.3641 | 62.2783 | 5.697 | 67.9753 | 14.8692 | 131.9077 | 123.3244 | 99.9567 | 14.8432 | 17.8307 | 191.5721 | 120.736 | 14.8311 | 1.2863 | 38.7514 | 74.8219 | 2.3315 | 0.15076 | 0.06982 | 18.5733 | 0.79635 | 0.34821
2025-06-08 23:00 | 34.6245 | 6.6307 | 0.86511 | 0.89863 | 17.3305 | 1.9945 | 12.3867 | 191.8998 | 17.6713 | 191.668 | 19.9299 | 36.3064 | 13.9833 | 198.1574 | 22.1068 | 37.8206 | 13.7641 | 195.7274 | 20.3646 | 38.0345 | 13.9375 | 196.4776 | 20.0074 | 40.5851 | 13.8937 | 197.3255 | 194.1902 | 13.002 | 52.8281 | 2.5749 | 9.9746 | 0 | 74.9785 | 21.1185 | 52.6696 | 13.1735 | 190.3527 | 193.5867 | 12.786 | 3.4129 | 61.6561 | 7.4034 | 69.0595 | 14.7433 | 131.0259 | 123.3045 | 99.9581 | 14.7178 | 17.6713 | 191.668 | 120.0934 | 14.6712 | 1.2893 | 38.1647 | 74.5555 | 0.30469 | 0.15259 | 0.069639 | 17.141 | 0.79694 | 0.3473
2025-06-09 | 33.9483 | 7.8446 | 0.88598 | 0.89847 | 17.7205 | 2.1035 | 12.4452 | 192.0901 | 17.6893 | 191.4017 | 20.0788 | 36.1139 | 14.0059 | 198.2276 | 22.2263 | 37.8257 | 13.7848 | 195.7839 | 20.0726 | 38.0375 | 13.941 | 196.405 | 20.0174 | 40.0521 | 13.9048 | 197.1769 | 194.2636 | 13.0288 | 52.2379 | 2.389 | 9.9766 | 0 | 74.8594 | 21.1081 | 52.2518 | 13.2136 | 190.3968 | 193.7431 | 12.837 | 3.2525 | 60.2804 | 11.1306 | 71.411 | 14.7148 | 132.4102 | 121.9137 | 99.9607 | 14.6884 | 17.6893 | 191.4017 | 120.6709 | 14.6944 | 1.2955 | 38.7979 | 75.4004 | 0.10737 | 0.1506 | 0.069441 | 19.9551 | 0.79748 | 0.34514
Total | MW: 827.6191; MVAR: 150.1151; kg/s: 4659169.913; kg/s: 285954.584; kg/s: 5215603.3797; kg/s: 553190.0623; kg/s: 5768793.4421; kg/s: 11290617.2488
Average | 34.4841 | 6.2548 | 0.90765 | 0.94797 | 19.2446 | 1.9362 | 12.3244 | 191.6627 | 17.6571 | 191.0978 | 19.9309 | 37.8101 | 14.0112 | 198.1616 | 22.1775 | 37.8959 | 13.768 | 195.7591 | 20.3203 | 38.2625 | 13.9339 | 196.1962 | 20.3376 | 41.3699 | 13.9147 | 197.1909 | 194.0342 | 12.9645 | 53.9256 | 2.8751 | 9.9736 | 0 | 75.8484 | 21.2858 | 52.6633 | 13.1176 | 190.1706 | 193.361 | 12.7256 | 3.3097 | 60.3658 | 6.4027 | 66.7684 | 14.7507 | 130.6784 | 124.0788 | 99.9625 | 14.7269 | 17.6571 | 191.0978 | 121.4811 | 14.6573 | 1.2852 | 37.7539 | 77.3864 | 1.8784 | 0.12606 | 0.075859 | 19.8233 | 0.77802 | 0.36538
Min | 33.9483 | 4.5381 | 0.84614 | 0.88789 | 17.3305 | 1.5965 | 12.1814 | 191.1355 | 17.5367 | 190.624 | 19.8333 | 36.1139 | 13.9021 | 197.7719 | 21.8704 | 36.6052 | 13.6525 | 195.3757 | 19.8409 | 38.0014 | 13.798 | 195.6225 | 19.8538 | 39.5032 | 13.7878 | 196.5635 | 193.5612 | 12.8343 | 52.2379 | 1.2626 | 9.9616 | 0 | 74.8594 | 21.1081 | 50.1294 | 13.0054 | 189.8214 | 192.8812 | 12.5898 | 3.0494 | 50.3031 | 4.5644 | 54.9461 | 14.6559 | 129.6992 | 121.9137 | 99.9566 | 14.6316 | 17.5367 | 190.624 | 120.0934 | 14.5369 | 1.1789 | 37.0036 | 74.5555 | 0.10737 | 0.1104 | 0.069441 | 16.5422 | 0.66271 | 0.34306
Max | 34.8787 | 7.8446 | 0.97779 | 1.0309 | 21.5962 | 2.1035 | 12.5393 | 192.4055 | 17.8307 | 191.7354 | 20.0788 | 38.1029 | 14.1659 | 198.6986 | 22.6555 | 38.9022 | 13.9347 | 196.264 | 20.7617 | 40.0228 | 14.1202 | 196.9684 | 20.8481 | 43.0696 | 14.0917 | 197.9316 | 194.7149 | 13.1663 | 54.9171 | 3.5417 | 9.9835 | 0 | 76.4324 | 21.443 | 55.2092 | 13.3092 | 190.7536 | 194.0575 | 12.9306 | 3.599 | 63.0836 | 11.1306 | 71.411 | 14.8813 | 132.4102 | 125.1904 | 99.9722 | 14.8557 | 17.8307 | 191.7354 | 122.7752 | 14.8311 | 1.4129 | 38.7979 | 80.0078 | 3.7108 | 0.15259 | 0.15661 | 21.6681 | 0.88826 | 0.46898

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day
18 |  | Night
19 | 2025-06-10 | Day
20 |  | Night
21 | 2025-06-11 | Day
22 |  | Night
23 | 2025-06-12 | Day
24 |  | Night
25 | 2025-06-13 | Day
26 |  | Night
27 | 2025-06-14 | Day
28 |  | Night
29 | 2025-06-15 | Day
30 |  | Night
31 | 2025-06-16 | Day
32 |  | Night
33 | 2025-06-17 | Day
34 |  | Night
35 | 2025-06-18 | Day
36 |  | Night
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-08
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0