## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-09
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 20.8796 | 199.0801 | 38.578
|  | #6-2 | Production | 22.904 | 196.766 | 38.5045
|  | #6-3 | Production | 20.4276 | 196.7682 | 37.8129
|  | #6-4 | Production | 20.4438 | 198.0895 | 40.4852
|  | #8-1 | Shut in | 1.7597 | 75.5299 | 9.9711
|  | #8-2 | Production | 21.5134 | 190.9345 | 49.3008
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 53.0713 | 4585356.2791
|  | PAD #8 - STEAM |  |  |  |  | 3.1916 | 275750.4107 | Online
|  | BRINE HEADER |  |  |  |  | 8.391 | 724982.8067 | Offline
|  | TOTAL FLOW |  |  |  |  | 64.6538 | 5586089.4965
|  | PRESS SEPARATOR IJN 6 | Online | 13.2032 | 194.8233
|  | PRESS SEPARATOR IJN 8 | Online | 12.9728 | 194.193
| INJECTION WELL | #5-1 | Injection | 14.8686 | 124.0449 | 99.967 | 132.3989 | 11439262.3696
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.5008 |  |  | 828.018
|  | NET | 31.793 |  |  | 763.032
| PARASITIC LOAD |  | 2.7078 |  |  | 64.986
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 1.874 |  |  | 6746.3382
|  | NET | 2.0336 |  |  | 7320.9114
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
8. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 9. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
10. DHP tools pull out at Well IJN 9-1 and Well IJN8-1 was done by Toptek. Master valve and crown valve closed
11. Brine Dump Control valve Ijen-6 PV-2227A indication passing

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-09
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 763031.9756 |  | 0 |  | 763031.9756
|  |  |  | 763031.9756 |  | 0 |  | 763031.9756
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 762840 | [7 empty] | 762840
M-T-D GROSS GENERATION (kWHR) |  |  |  | 7441110 | [7 empty] | 7441110
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 17921.66 | 0 | 6387.07 | 42 | 1117 | 1446 | 26913.73
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 164850.46 | -283254.3 | 54647.18 | 391.5 | 11880 | 14420 | 81338.68
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.5008 |  |  | 6.231 |  | 18.4885
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 216
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 92.16%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 4585.3563 |  | 275.7504 |  |  | 5154.4288
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.053071 |  | 0.0031916 |  |  | 0.059658
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 724.9828
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.008391
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 5879.4116
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.068049
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 192.582 |  |  |  | 192.0758
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.5914 |  |  |  | 17.8576
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 16.8252 |  | 20.2425 |  |  | 18.4885
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:02 | PLN adviced load ROH 31.72 MW (Mr. Gendhon Suhendro)
2:33 | Turn off ACC Fan F-9302 due to reduce high vibration in turbine CW side
2:34 | Start pit pump IJN 8 (Level pond : 34.1%)
5:37 | Stop pit pump IJN 8 (Level pond : 28.2%)
6:00 | Switchyard visual inspection (Standart activities schedule)
6:52 | PLN adviced load ROH 31.72 MW (Mr. Eko Safi)
10:35 | Start P8501 backwash pump and already rinsing (Standard activity)
10:49 | auto start of jockey pump --> Pressure system : 9.6 Bar and not blinking for electrical panel (still auto mode)
10:53 | Running test compressor-B (Standard Activity)
14:47 | Start pit pump IJN 8 (Level pond : 39.4%)
16:11 | Preparation install corrosion coupon at IJN-5 by SOLENIS
16:45 | Check and Release Pressure & Condensate Master Valve & Wing Valve PW IJN 9-1 (Standard Activities)
17:04 | Check and Release Pressure & Condensate Master Valve & Wing Valve PW IJN 2-1 (Standard Activities)
17:13 | Stop pit pump IJN 8 (Level pond : 34.9%)
17:15 | Start electrical pit pump IJN-6 (level pond : 44.7%) (Discharge Pressure : 18.5 Bar)
19:21 | Stop electrical pit pump IJN-6 (Level pond : 45.1%)
19:24 | Start pit pump IJN-8 (Level pond : 37.9%)
21:54 | Stop pit pump IJN 8 (Level pond : 33.3%)
21:55 | Start electrical pit pump IJN-6 (level pond : 50.4%) (Discharge Pressure: 17.7Bar and Current: 93 A)
21:40 | Cleaning MCC Room IJN 8
22:05 | Cleaning MCC Room IJN 6
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Arbima |  |  |  | CCR Operator : Dwiki |  |  |  | Steamfield : Rafly
Night Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Tio |  |  |  | Steamfield : Dede
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-09
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2182760 | 2187090 | 4330 | 59240
(BACKUP) |  | 2126290 | 2181130 | 2185460 | 4330 | 59170
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 99177930 | 99940770 | 762840 | 6838860
(BACKUP) |  | 93082960 | 99157260 | 99919890 | 762630 | 6836930
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4376430 | 4416640 | 40210 | 274410
(BACKUP) |  | 4144060 | 4378350 | 4418560 | 40210 | 274500
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 107935726 | 108764365 | 828639 | 7441110
TOTAL |  |  |  |  | 828639 | 7441110
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 17607996 | 17757678 | 149682 | 1227423
TOTAL |  |  |  |  | 149682 | 1227423
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3236247.14 | 3254168.8 | 17921.66 | 164850.46
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1038018.52 | 1044405.59 | 6387.07 | 54647.18
U Ijen 5 |  | 7258.6 | 7608.1 | 7650.1 | 42 | 391.5
U Ijen 6 |  | 247889 | 258652 | 259769 | 1117 | 11880
U Ijen 8 |  | 299837 | 312811 | 314257 | 1446 | 14420
TOTAL |  |  |  |  | 26913.73 | 246189.14
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-09 01:00 | 34.3889 | 4.578 | 0.87003 | 0.88782 | 17.0869 | 2.0081 | 12.4593 | 192.145 | 17.7449 | 191.6862 | 19.8964 | 36.8575 | 14.0562 | 198.3833 | 22.4143 | 37.82 | 13.8395 | 196.0187 | 20.5198 | 38.0331 | 14.0103 | 196.6069 | 20.4 | 40.0542 | 13.9672 | 197.3719 | 194.3851 | 13.0636 | 52.6753 | 2.0371 | 9.9723 | 0 | 74.751 | 21.082 | 52.2597 | 13.2315 | 190.5047 | 193.81 | 12.8529 | 3.2035 | 61.0439 | 8.0125 | 69.0564 | 14.7981 | 131.9488 | 123.438 | 99.9588 | 14.7722 | 17.7449 | 191.6862 | 120.6758 | 14.7445 | 1.2948 | 38.5291 | 75.1573 | 1.7998 | 0.14715 | 0.069758 | 17.6928 | 0.80635 | 0.34445
2025-06-09 02:00 | 34.6411 | 3.413 | 0.86277 | 0.88052 | 16.8252 | 1.996 | 12.4593 | 192.1426 | 17.7588 | 191.9007 | 19.7865 | 37.8448 | 14.0631 | 198.4062 | 22.042 | 37.8199 | 13.8384 | 196.0135 | 20.6138 | 38.0347 | 14.0149 | 196.554 | 20.4768 | 40.0522 | 13.9734 | 197.4559 | 194.4046 | 13.0702 | 53.002 | 1.7981 | 9.9685 | 0 | 74.648 | 21.0869 | 52.2613 | 13.2314 | 190.5091 | 193.8077 | 12.8542 | 3.1281 | 61.4204 | 7.7247 | 69.1451 | 14.82 | 131.706 | 123.5162 | 99.9587 | 14.794 | 17.7588 | 191.9007 | 120.2853 | 14.7586 | 1.2962 | 38.3521 | 74.6968 | 1.0628 | 0.15369 | 0.069428 | 18.2339 | 0.81181 | 0.34616
2025-06-09 03:00 | 34.4407 | 3.3048 | 0.87589 | 0.8866 | 17.215 | 2.0129 | 12.4298 | 192.0404 | 17.7237 | 191.9074 | 19.7226 | 38.0846 | 14.029 | 198.3063 | 22.177 | 37.8215 | 13.8061 | 195.9475 | 20.3029 | 38.0361 | 13.9615 | 196.2458 | 20.4544 | 40.0522 | 13.9385 | 197.3438 | 194.3 | 13.0391 | 52.7696 | 1.7375 | 9.9677 | 0 | 74.5596 | 21.0887 | 52.2806 | 13.2052 | 190.43 | 193.707 | 12.8252 | 3.1864 | 61.3686 | 7.9557 | 69.3243 | 14.784 | 131.5208 | 123.1779 | 99.959 | 14.7579 | 17.7237 | 191.9074 | 120.4244 | 14.7237 | 1.297 | 38.3852 | 74.861 | 0.60012 | 0.15428 | 0.069391 | 17.9905 | 0.8084 | 0.34786
2025-06-09 04:00 | 34.2549 | 3.7036 | 0.88387 | 0.88488 | 17.4294 | 2.0327 | 12.4109 | 191.9793 | 17.6963 | 191.8583 | 19.6968 | 38.0835 | 14.0068 | 198.2291 | 22.0927 | 37.8223 | 13.7798 | 195.8654 | 20.2254 | 38.0347 | 13.9324 | 196.0226 | 20.4841 | 40.0535 | 13.9173 | 197.2841 | 194.2216 | 13.0142 | 52.5355 | 1.7715 | 9.9633 | 0 | 74.4965 | 21.0867 | 52.2975 | 13.1882 | 190.3903 | 193.6444 | 12.8052 | 3.1987 | 61.2699 | 8.3592 | 69.6291 | 14.7672 | 131.3239 | 123.5362 | 99.9599 | 14.7413 | 17.6963 | 191.8583 | 120.6074 | 14.6963 | 1.2944 | 38.2485 | 75.3129 | 1.4451 | 0.14787 | 0.069607 | 17.7376 | 0.80215 | 0.34791
2025-06-09 05:00 | 34.5395 | 4.4276 | 0.87537 | 0.88465 | 17.4776 | 2.0032 | 12.4492 | 192.1116 | 17.7478 | 191.7881 | 19.6887 | 38.0833 | 14.0608 | 198.3982 | 22.0616 | 37.8252 | 13.8359 | 196.027 | 20.5976 | 38.0335 | 14.0033 | 196.1744 | 20.4818 | 40.9344 | 13.9914 | 197.5244 | 194.3695 | 13.0589 | 52.9581 | 1.7908 | 9.961 | 0 | 74.4477 | 21.0838 | 52.7439 | 13.2254 | 190.4912 | 193.7774 | 12.8445 | 3.1373 | 61.5187 | 7.672 | 69.1907 | 14.8113 | 131.6134 | 123.6667 | 99.9601 | 14.7852 | 17.7478 | 191.7881 | 120.5415 | 14.7476 | 1.2931 | 38.3365 | 75.1742 | 2.4175 | 0.14662 | 0.069552 | 18.2782 | 0.79982 | 0.34748
2025-06-09 06:00 | 34.8653 | 5.8225 | 0.87033 | 0.89131 | 17.4923 | 1.9794 | 12.4953 | 192.2756 | 17.8014 | 191.8481 | 19.6765 | 37.9916 | 14.1131 | 198.5703 | 22.2803 | 37.8263 | 13.8948 | 196.2374 | 20.6782 | 38.0344 | 14.055 | 196.4334 | 20.4793 | 41.1307 | 14.0498 | 197.8027 | 194.5683 | 13.1169 | 53.4939 | 1.756 | 9.9666 | 0 | 74.4272 | 21.0866 | 51.062 | 13.2699 | 190.6418 | 193.9346 | 12.8913 | 3.0821 | 62.157 | 6.8541 | 69.0112 | 14.8531 | 131.9955 | 123.4643 | 99.9609 | 14.8268 | 17.8014 | 191.8481 | 120.4433 | 14.8009 | 1.2887 | 38.5262 | 74.7067 | 1.6142 | 0.14293 | 0.069837 | 18.6825 | 0.79576 | 0.34994
2025-06-09 07:00 | 34.6412 | 7.2357 | 0.84834 | 0.88314 | 17.8348 | 1.8086 | 12.4331 | 192.0517 | 17.7089 | 191.9301 | 19.6547 | 37.908 | 14.0249 | 198.2863 | 22.3233 | 37.8208 | 13.8063 | 195.9756 | 20.2963 | 38.0204 | 13.9285 | 196.1698 | 20.2995 | 40.2485 | 13.9478 | 197.521 | 194.3192 | 13.0445 | 52.9987 | 1.7367 | 9.9736 | 0 | 74.4902 | 21.1192 | 48.6153 | 13.2129 | 190.5069 | 193.6979 | 12.8265 | 3.0807 | 54.6613 | 7.9914 | 62.6527 | 14.776 | 131.7624 | 123.2668 | 99.9663 | 14.7506 | 17.7089 | 191.9301 | 120.2362 | 14.7085 | 1.2537 | 38.3077 | 74.7086 | 0.3623 | 0.12723 | 0.0718 | 17.6586 | 0.78018 | 0.35835
2025-06-09 08:00 | 34.4494 | 7.3221 | 0.83478 | 0.86454 | 18.772 | 1.6239 | 12.3909 | 191.9088 | 17.653 | 191.9 | 19.6449 | 37.9976 | 14.0047 | 198.1534 | 22.5218 | 37.8318 | 13.778 | 195.8895 | 20.2767 | 37.9957 | 13.8734 | 196.0311 | 20.2773 | 40.0655 | 13.9111 | 197.3241 | 194.1567 | 12.9974 | 52.6603 | 1.7789 | 9.9765 | 0 | 74.7314 | 21.1789 | 48.2469 | 13.1849 | 190.5151 | 193.5436 | 12.7817 | 3.1467 | 47.6491 | 8.2932 | 55.9423 | 14.7326 | 132.1605 | 123.1528 | 99.9748 | 14.71 | 17.653 | 191.9 | 120.2468 | 14.6528 | 1.1939 | 38.1561 | 74.9861 | 1.23 | 0.11466 | 0.075438 | 17.3773 | 0.74984 | 0.35809
2025-06-09 09:00 | 33.6225 | 7.1563 | 0.82915 | 0.84512 | 19.5053 | 1.7984 | 12.3634 | 191.8086 | 17.5853 | 191.6619 | 19.6976 | 38.111 | 13.9985 | 197.9429 | 22.5019 | 37.8536 | 13.7623 | 195.8016 | 20.7128 | 38.0225 | 13.89 | 196.0166 | 20.5306 | 40.0814 | 13.891 | 197.2356 | 193.953 | 12.943 | 51.4539 | 1.8601 | 9.9798 | 0 | 75.099 | 21.2218 | 48.3759 | 13.1622 | 190.5023 | 193.4217 | 12.7448 | 3.9757 | 49.5229 | 10.943 | 60.4659 | 14.4476 | 131.193 | 123.0714 | 99.9796 | 14.4271 | 17.5853 | 191.6619 | 120.5902 | 14.5855 | 1.1697 | 37.1888 | 76.0135 | 9.9364 | 0.11417 | 0.077609 | 15.9099 | 0.7276 | 0.34814
2025-06-09 10:00 | 32.7764 | 6.935 | 0.83387 | 0.85286 | 20.0601 | 2.0293 | 12.386 | 191.8613 | 17.5658 | 191.7342 | 20.3159 | 38.6053 | 14.0734 | 198.061 | 22.0633 | 38.2647 | 13.8105 | 195.9242 | 20.7579 | 39.2466 | 13.9787 | 196.2979 | 20.5134 | 40.73 | 13.9499 | 197.4014 | 193.9036 | 12.9392 | 50.2798 | 1.8544 | 9.9853 | 0 | 75.4717 | 21.2492 | 51.2578 | 13.1808 | 190.5789 | 193.4516 | 12.7591 | 3.9808 | 53.589 | 12.9237 | 66.5127 | 14.419 | 131.4995 | 123.3044 | 99.9827 | 14.3982 | 17.5658 | 191.7342 | 121.9458 | 14.5657 | 1.1615 | 37.5251 | 77.7593 | 19.0915 | 0.11592 | 0.078474 | 14.2913 | 0.70778 | 0.34838
2025-06-09 11:00 | 33.9993 | 6.4816 | 0.85673 | 0.87642 | 20.2425 | 2.0202 | 12.5472 | 192.4152 | 17.7885 | 191.9682 | 21.3509 | 39.3149 | 14.4079 | 199.0963 | 21.9019 | 38.8437 | 14.0933 | 196.8251 | 20.6318 | 40.7346 | 14.2881 | 197.2574 | 20.5186 | 42.228 | 14.2443 | 198.3515 | 194.5878 | 13.1447 | 52.1142 | 1.6325 | 9.9895 | 0 | 75.8301 | 21.276 | 53.5334 | 13.3395 | 191.0902 | 194.0129 | 12.9242 | 3.1472 | 59.3211 | 9.3645 | 68.6856 | 14.8609 | 133.3419 | 124.4938 | 99.9831 | 14.8401 | 17.7885 | 191.9682 | 122.2113 | 14.7884 | 1.1592 | 38.7072 | 77.4014 | 20.0382 | 0.11633 | 0.079128 | 17.0868 | 0.68877 | 0.34741
2025-06-09 12:00 | 35.0273 | 6.5773 | 0.86681 | 0.88386 | 19.7994 | 1.9565 | 12.6883 | 192.8866 | 17.9808 | 192.1161 | 21.9433 | 39.3413 | 14.61 | 199.8006 | 22.274 | 39.015 | 14.2892 | 197.4531 | 20.2419 | 41.0427 | 14.475 | 197.7353 | 20.4127 | 43.075 | 14.4399 | 199.0182 | 195.1719 | 13.3206 | 53.6986 | 1.3564 | 9.9832 | 0 | 75.981 | 21.2803 | 52.5997 | 13.4568 | 191.4098 | 194.5008 | 13.07 | 3.1003 | 61.4366 | 7.0939 | 68.5305 | 15.0262 | 133.5271 | 124.595 | 99.9768 | 15.0033 | 17.9808 | 192.1161 | 122.0139 | 14.9807 | 1.2021 | 38.9843 | 76.3889 | 17.4512 | 0.11297 | 0.076189 | 19.1859 | 0.84805 | 0.34422
2025-06-09 13:00 | 34.8364 | 7.4386 | 0.85543 | 0.86805 | 19.4238 | 1.94 | 12.7183 | 193.0107 | 18.002 | 192.5286 | 22.1029 | 39.119 | 14.595 | 199.8746 | 22.4965 | 38.9919 | 14.2903 | 197.4859 | 19.7632 | 41.0517 | 14.4478 | 197.6245 | 20.1072 | 43.0682 | 14.4372 | 199.0409 | 195.2835 | 13.3451 | 53.4945 | 1.2388 | 9.9742 | 0 | 75.9666 | 21.3105 | 51.0551 | 13.4498 | 191.4324 | 194.6116 | 13.0956 | 3.0579 | 60.2294 | 7.3521 | 67.5815 | 15.0394 | 133.4118 | 124.7524 | 99.9727 | 15.0151 | 18.002 | 192.5286 | 122.1044 | 15.0014 | 1.2397 | 38.9558 | 76.0119 | 15.7948 | 0.11116 | 0.072429 | 18.8326 | 0.94162 | 0.34559
2025-06-09 14:00 | 34.821 | 7.6531 | 0.83553 | 0.8451 | 19.1906 | 1.9968 | 12.7221 | 193.0532 | 17.9912 | 192.683 | 22.1441 | 39.112 | 14.5718 | 199.835 | 22.4124 | 38.9732 | 14.2653 | 197.4386 | 20.029 | 39.8566 | 14.3984 | 197.5099 | 20.0395 | 42.0459 | 14.3903 | 198.915 | 195.3076 | 13.3419 | 53.2061 | 1.2451 | 9.9731 | 0 | 76.0154 | 21.4559 | 48.1853 | 13.4332 | 191.392 | 194.6239 | 13.0905 | 3.0814 | 60.2454 | 9.2865 | 69.5318 | 15.041 | 133.4916 | 124.7778 | 99.9752 | 15.018 | 17.9912 | 192.683 | 121.5919 | 14.991 | 1.2384 | 38.7854 | 75.2845 | 13.0953 | 0.11117 | 0.071642 | 18.3408 | 0.83919 | 0.3468
2025-06-09 15:00 | 34.6371 | 6.6439 | 0.82036 | 0.83255 | 18.7816 | 2.0398 | 12.6932 | 192.9326 | 17.9462 | 192.6576 | 22.1972 | 39.1048 | 14.5218 | 199.636 | 22.8527 | 38.9734 | 14.2127 | 197.2826 | 19.907 | 38.326 | 14.3043 | 197.2152 | 20.0789 | 41.0424 | 14.3049 | 198.6021 | 195.1443 | 13.2989 | 52.8049 | 1.2603 | 9.9725 | 0 | 76.1477 | 21.692 | 47.2228 | 13.4057 | 191.2298 | 194.4826 | 13.0562 | 3.0093 | 60.6336 | 10.0182 | 70.6518 | 14.9934 | 133.6223 | 124.0466 | 99.9777 | 14.9711 | 17.9462 | 192.6576 | 121.7876 | 14.9461 | 1.2241 | 38.9385 | 75.4949 | 10.4776 | 0.11018 | 0.071965 | 18.0231 | 0.80046 | 0.34517
2025-06-09 16:00 | 34.5552 | 5.9412 | 0.80504 | 0.81791 | 18.0854 | 2.0229 | 12.6894 | 192.8914 | 17.9353 | 192.6226 | 22.2379 | 39.1076 | 14.5155 | 199.5942 | 23.344 | 38.9728 | 14.2123 | 197.2689 | 19.6703 | 37.9954 | 14.2909 | 197.0487 | 20.2438 | 41.0575 | 14.3015 | 198.5383 | 195.0813 | 13.2894 | 52.5506 | 1.336 | 9.9711 | 0 | 76.2662 | 21.8713 | 48.0971 | 13.4037 | 191.1788 | 194.4444 | 13.0519 | 3.0028 | 60.6403 | 9.261 | 69.9013 | 14.9862 | 133.3891 | 124.2812 | 99.9754 | 14.9628 | 17.9353 | 192.6226 | 121.6871 | 14.9348 | 1.2348 | 38.8436 | 75.5052 | 12.0005 | 0.11089 | 0.071634 | 17.7918 | 0.81261 | 0.34276
2025-06-09 17:00 | 34.7181 | 6.7405 | 0.80719 | 0.81944 | 17.7581 | 2.0144 | 12.7472 | 193.1162 | 17.9998 | 192.6918 | 22.2026 | 39.1125 | 14.5623 | 199.8061 | 23.6213 | 38.9732 | 14.2755 | 197.4989 | 20.3493 | 37.4005 | 14.36 | 197.1604 | 20.3946 | 40.258 | 14.3561 | 198.678 | 195.3278 | 13.3548 | 52.8258 | 1.5441 | 9.9709 | 0 | 76.3068 | 21.9679 | 46.0634 | 13.4507 | 191.3417 | 194.6699 | 13.1103 | 3.1362 | 61.0953 | 8.8418 | 69.9372 | 15.0345 | 133.42 | 124.0993 | 99.9705 | 15.0093 | 17.9998 | 192.6918 | 121.1168 | 14.9995 | 1.2526 | 39.0315 | 74.286 | 11.4376 | 0.11664 | 0.07075 | 17.9678 | 1.0278 | 0.34257
2025-06-09 18:00 | 34.6883 | 7.4453 | 0.85673 | 0.86845 | 18.1046 | 1.9933 | 12.7366 | 193.0904 | 18.014 | 192.4937 | 22.1713 | 39.1057 | 14.5544 | 199.8153 | 24.2712 | 38.9768 | 14.2847 | 197.5283 | 20.6363 | 36.9202 | 14.3577 | 197.1079 | 20.3466 | 39.7588 | 14.3418 | 198.4104 | 195.3348 | 13.3533 | 53.9075 | 1.7791 | 9.9714 | 0 | 76.3007 | 22.0322 | 45.6857 | 13.4494 | 191.2796 | 194.6663 | 13.1073 | 3.1946 | 61.6752 | 7.4688 | 69.144 | 15.034 | 133.2537 | 123.6225 | 99.9644 | 15.008 | 18.014 | 192.4937 | 121.508 | 15.0139 | 1.2537 | 39.2724 | 74.5475 | 9.2561 | 0.12874 | 0.069856 | 18.4993 | 1.0241 | 0.34182
2025-06-09 19:00 | 34.434 | 7.1925 | 0.89167 | 0.91649 | 18.7041 | 1.9939 | 12.6567 | 192.8141 | 17.9476 | 192.3 | 22.1198 | 39.0871 | 14.4742 | 199.5903 | 24.2688 | 38.9833 | 14.2079 | 197.2914 | 20.2979 | 37.0423 | 14.2752 | 196.8431 | 20.5132 | 40.0584 | 14.2738 | 197.9335 | 195.0617 | 13.2712 | 53.962 | 1.913 | 9.9699 | 0 | 76.2678 | 22.0187 | 48.0552 | 13.3862 | 191.0465 | 194.4181 | 13.0346 | 3.0988 | 61.4225 | 7.2352 | 68.6577 | 14.992 | 132.3268 | 124.2769 | 99.9591 | 14.9663 | 17.9476 | 192.3 | 121.9742 | 14.9476 | 1.2493 | 38.8356 | 75.7862 | 9.8515 | 0.1342 | 0.069435 | 18.704 | 0.78256 | 0.34253
2025-06-09 20:00 | 34.4609 | 7.2223 | 0.90357 | 0.93717 | 18.9455 | 1.9738 | 12.6663 | 192.8676 | 17.9699 | 192.188 | 22.0732 | 39.0765 | 14.4926 | 199.6629 | 24.2268 | 38.9858 | 14.2277 | 197.389 | 20.4894 | 37.0425 | 14.3002 | 196.9183 | 20.6995 | 39.9865 | 14.3042 | 198.2298 | 195.1387 | 13.2884 | 53.6273 | 1.9646 | 9.9669 | 0 | 76.2347 | 21.9712 | 47.8362 | 13.3963 | 191.0684 | 194.4728 | 13.0452 | 3.1148 | 61.2555 | 6.7628 | 68.0182 | 15.0255 | 132.0589 | 124.8709 | 99.9577 | 15.0001 | 17.9699 | 192.188 | 122.0816 | 14.9701 | 1.2413 | 38.6494 | 76.1569 | 10.0694 | 0.1336 | 0.069547 | 19.4934 | 0.89252 | 0.34357
2025-06-09 21:00 | 34.7658 | 6.5997 | 0.91803 | 0.94925 | 18.9309 | 1.9465 | 12.7854 | 193.2708 | 17.9947 | 191.669 | 21.5875 | 39.0777 | 14.5729 | 199.9391 | 24.4307 | 38.9853 | 14.3193 | 197.6687 | 21.0762 | 35.4686 | 14.3779 | 197.202 | 20.8032 | 37.7413 | 14.3632 | 198.7838 | 195.6091 | 13.4311 | 54.522 | 2.0703 | 9.9647 | 0 | 76.183 | 22.0259 | 42.055 | 13.4828 | 191.2885 | 194.8317 | 13.1568 | 3.244 | 61.7562 | 5.9156 | 67.6718 | 15.0321 | 132.0219 | 124.9422 | 99.959 | 15.0067 | 17.9947 | 191.669 | 122.3011 | 14.9947 | 1.2385 | 38.4768 | 76.4076 | 5.222 | 0.13534 | 0.069635 | 16.5694 | 1.0508 | 0.34367
2025-06-09 22:00 | 34.624 | 6.4524 | 0.91495 | 0.94392 | 18.8994 | 1.9775 | 12.6916 | 192.9441 | 17.8897 | 191.6424 | 20.7047 | 39.0789 | 14.4072 | 199.463 | 23.9465 | 39.2583 | 14.164 | 197.1257 | 20.8192 | 33.8014 | 14.2079 | 196.6907 | 20.6141 | 37.8094 | 14.2081 | 198.2281 | 195.2746 | 13.3315 | 54.5111 | 2.204 | 9.9642 | 0 | 76.1109 | 22.1619 | 43.3544 | 13.4133 | 191.0782 | 194.5279 | 13.0695 | 3.1625 | 62.4754 | 5.9927 | 68.4681 | 14.9443 | 131.6647 | 125.1371 | 99.9591 | 14.9192 | 17.8897 | 191.6424 | 122.4482 | 14.8899 | 1.2388 | 38.1749 | 77.0243 | 0.67401 | 0.1373 | 0.069743 | 15.4716 | 0.90919 | 0.34198
2025-06-09 23:00 | 34.783 | 6.5595 | 0.91146 | 0.94359 | 18.9479 | 1.9812 | 12.6413 | 192.7601 | 17.9544 | 191.7673 | 20.2629 | 38.6118 | 14.3379 | 199.2514 | 23.8183 | 39.4017 | 14.1201 | 196.9967 | 20.4247 | 34.3484 | 14.1667 | 196.472 | 20.6066 | 40.0544 | 14.2035 | 198.1468 | 195.0733 | 13.274 | 54.2176 | 2.2814 | 9.9634 | 0 | 76.0287 | 22.1001 | 49.8673 | 13.4101 | 191.0501 | 194.4064 | 13.035 | 3.1116 | 63.354 | 5.5572 | 68.9111 | 15.0147 | 132.0591 | 125.2809 | 99.9589 | 14.9891 | 17.9544 | 191.7673 | 122.4277 | 14.9541 | 1.2367 | 38.4947 | 76.9848 | 0.37069 | 0.13686 | 0.069891 | 19.1405 | 0.75688 | 0.34234
2025-06-10 | 35.0478 | 6.6964 | 0.90219 | 0.92654 | 18.212 | 2.1841 | 12.9332 | 193.5905 | 18.1818 | 192.2768 | 20.2304 | 38.0558 | 14.5719 | 199.8205 | 23.3527 | 38.068 | 14.3625 | 197.4307 | 20.9444 | 34.9872 | 14.4327 | 197.0997 | 20.8753 | 40.0597 | 14.4702 | 199.0056 | 195.7816 | 13.5444 | 53.4411 | 2.2858 | 9.9557 | 0 | 75.9556 | 21.8741 | 50.2089 | 13.6634 | 191.4716 | 195.1659 | 13.3146 | 3.0157 | 62.0444 | 14.5044 | 76.5488 | 15.1994 | 133.2602 | 124.3055 | 99.9587 | 15.1729 | 18.1818 | 192.2768 | 122.1117 | 15.1845 | 1.2283 | 39.0072 | 76.1745 | 0.12765 | 0.12802 | 0.070653 | 14.2721 | 0.74984 | 0.34561
Total | MW: 828.018; MVAR: 149.5429; kg/s: 4585356.2791; kg/s: 275750.4107; kg/s: 5154428.7599; kg/s: 724982.8067; kg/s: 5879411.5666; kg/s: 11439262.3696
Average | 34.5008 | 6.231 | 0.86375 | 0.88292 | 18.4885 | 1.9722 | 12.5914 | 192.582 | 17.8576 | 192.0758 | 20.8796 | 38.578 | 14.3177 | 199.0801 | 22.904 | 38.5045 | 14.0615 | 196.766 | 20.4276 | 37.8129 | 14.1805 | 196.7682 | 20.4438 | 40.4852 | 14.174 | 198.0895 | 194.8233 | 13.2032 | 53.0713 | 1.7597 | 9.9711 | 0 | 75.5299 | 21.5134 | 49.3008 | 13.3431 | 190.9345 | 194.193 | 12.9728 | 3.1916 | 59.6577 | 8.391 | 68.0487 | 14.893 | 132.3989 | 124.0449 | 99.967 | 14.8686 | 17.8576 | 192.0758 | 121.3901 | 14.8575 | 1.2408 | 38.5297 | 75.7013 | 7.3094 | 0.12866 | 0.071808 | 17.6347 | 0.82976 | 0.34637
Min | 32.7764 | 3.3048 | 0.80504 | 0.81791 | 16.8252 | 1.6239 | 12.3634 | 191.8086 | 17.5658 | 191.6424 | 19.6449 | 36.8575 | 13.9985 | 197.9429 | 21.9019 | 37.8199 | 13.7623 | 195.8016 | 19.6703 | 33.8014 | 13.8734 | 196.0166 | 20.0395 | 37.7413 | 13.891 | 197.2356 | 193.9036 | 12.9392 | 50.2798 | 1.2388 | 9.9557 | 0 | 74.4272 | 21.082 | 42.055 | 13.1622 | 190.3903 | 193.4217 | 12.7448 | 3.0028 | 47.6491 | 5.5572 | 55.9423 | 14.419 | 131.193 | 123.0714 | 99.9577 | 14.3982 | 17.5658 | 191.6424 | 120.2362 | 14.5657 | 1.1592 | 37.1888 | 74.286 | 0.12765 | 0.11018 | 0.069391 | 14.2721 | 0.68877 | 0.34182
Max | 35.0478 | 7.6531 | 0.91803 | 0.94925 | 20.2425 | 2.1841 | 12.9332 | 193.5905 | 18.1818 | 192.6918 | 22.2379 | 39.3413 | 14.61 | 199.9391 | 24.4307 | 39.4017 | 14.3625 | 197.6687 | 21.0762 | 41.0517 | 14.475 | 197.7353 | 20.8753 | 43.075 | 14.4702 | 199.0409 | 195.7816 | 13.5444 | 54.522 | 2.2858 | 9.9895 | 0 | 76.3068 | 22.1619 | 53.5334 | 13.6634 | 191.4716 | 195.1659 | 13.3146 | 3.9808 | 63.354 | 14.5044 | 76.5488 | 15.1994 | 133.6223 | 125.2809 | 99.9831 | 15.1729 | 18.1818 | 192.6918 | 122.4482 | 15.1845 | 1.297 | 39.2724 | 77.7593 | 20.0382 | 0.15428 | 0.079128 | 19.4934 | 1.0508 | 0.35835

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1
18 |  | Night | 22:15 | 5.55 | 22.2
19 | 2025-06-10 | Day
20 |  | Night
21 | 2025-06-11 | Day
22 |  | Night
23 | 2025-06-12 | Day
24 |  | Night
25 | 2025-06-13 | Day
26 |  | Night
27 | 2025-06-14 | Day
28 |  | Night
29 | 2025-06-15 | Day
30 |  | Night
31 | 2025-06-16 | Day
32 |  | Night
33 | 2025-06-17 | Day
34 |  | Night
35 | 2025-06-18 | Day
36 |  | Night
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-09
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0