## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-10
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 21.1077 | 199.3217 | 39.0828
|  | #6-2 | Production | 21.1695 | 196.8172 | 39.3236
|  | #6-3 | Production | 20.4634 | 196.9448 | 38.9904
|  | #6-4 | Production | 20.2562 | 198.3659 | 41.6598
|  | #8-1 | Shut in | 2.894 | 75.8912 | 9.9737
|  | #8-2 | Production | 21.4005 | 191.1771 | 52.0893
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 53.4699 | 4619795.6211
|  | PAD #8 - STEAM |  |  |  |  | 3.2158 | 277843.8845 | Online
|  | BRINE HEADER |  |  |  |  | 7.1408 | 616968.6779 | Offline
|  | TOTAL FLOW |  |  |  |  | 63.8265 | 5514608.1835
|  | PRESS SEPARATOR IJN 6 | Online | 11.8217 | 194.9813
|  | PRESS SEPARATOR IJN 8 | Online | 13.0162 | 194.3537
| INJECTION WELL | #5-1 | Injection | 15.0383 | 124.7104 | 99.9636 | 132.0516 | 11409258.8492
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.4218 |  |  | 826.1225
|  | NET | 31.7287 |  |  | 761.4882
| PARASITIC LOAD |  | 2.6931 |  |  | 64.6343
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 1.8542 |  |  | 6675.2908
|  | NET | 2.0116 |  |  | 7241.8824
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-10
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 761488.2226 |  | 0 |  | 761488.2226
|  |  |  | 761488.2226 |  | 0 |  | 761488.2226
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 761070 | [7 empty] | 761070
M-T-D GROSS GENERATION (kWHR) |  |  |  | 8268907 | [7 empty] | 8268907
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18207.01 | 0 | 5446.37 | 43.5 | 1352 | 1531 | 26579.88
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 183057.47 | -283254.3 | 60093.55 | 435 | 13232 | 15951 | 89711.55
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.4218 |  |  | 7.0859 |  | 19.2575
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 240
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 91.98%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 4619.7956 |  | 277.8439 |  |  | 5044.7003
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.05347 |  | 0.0032158 |  |  | 0.058388
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 616.9687
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.0071408
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 5661.6689
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.065529
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 192.711 |  |  |  | 192.0948
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.6263 |  |  |  | 17.9125
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 18.1768 |  | 21.0028 |  |  | 19.2575
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:11 | PLN adviced load ROH 31.72 MW (Mr. Eko Safii)
1:13 | Stop electrical pit pump IJN-6 (Level pond : 39.9%)
1:14 | Start pit pump IJN 8 (Level pond : 37.1%)
4:36 | Stop pit pump IJN 8 (Level pond : 32.2%)
4:37 | Start electrical pit pump IJN-6 (Level pond : 40.7%)
7:20 | Stop electrical pit pump IJN-6 (Level pond : 30.5%)
7:55 | Changeover compressor -A to B due to found problem on bearing pump --> Still investigation by maintenance team
9:25 | Exercise all master valve at IJN 6 (6.1, 6.2, 6.3, 6.4) --> Result : good and normal (Standard Activity)
9:43 | Start Reinjection Pump-B due to changeover of Reinjection pump (Standard Activity) --> Speed : 1334 Rpm and result : Good and normal condition
9:46 | Stop Reinjection Pump-A
9:52 | Cleaning PT-2006B (PW IJN 6.2) due to abnormal reading by I&C maintenance team --> Indication blockage at manifold
10:10 | Start pit pump IJN-8 (Level pond : 39.5%) (Discharge Pressure : 21.5 Bar)
10:53 | Flushing FT-2220 (steam flow transmitter IJN-6) by I&C team
11:23 | Flushing PT-2208 (WP IJN 6.2) by I&C team --> Indication blockage at manifold
11:55 | Start top up service water tank around 5000 ltr (1 tank) --> Level before : 39.78%
11:57 | Install scalling coupon by subsurface team and solenis team on IJN-5
13:03 | Top up service water already done with 2 tanks (@5000 ltr) -->Level after: 41.03%
13:40 | Stop pit pump IJN-8 (Level pond : 32.9%)
14:01 | Top up seal oil tank around 13.2 Ltr --> Level before : 70%. Level after : 81%
15:27 | Start compressor-A due to check bearing problem with IKPT Team
15:37 | Running unload test of Emergency Diesel Generator (EDG)
15:51 | Stop EDG by auto
16:32 | Start electrical pit pump IJN-6 (Level pond : 48.9%)
16:45 | Check & drain condensate drain pot (CDP) on IJN-6&8
19:15 | Stop electrical pit pump IJN-6 (Level pond : 49.6%)
19:16 | Start pit pump IJN-8 (Level pond : 39.9%)
21:35 | Check condition pit pump IJN-8 with pressure: 21.6bar and current: 125A
21:48 | Stop pit pump IJN-8 (Level pond : 34.8%)
21:48 | Start electrical pit pump IJN-6 (Level pond : 56.4%) --> P : 17.9bar & A : 93
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Arbima |  |  |  | CCR Operator : Dwiki |  |  |  | Steamfield : Rafly
Night Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Tio |  |  |  | Steamfield : Dede
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-10
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2187090 | 2187420 | 330 | 59570
(BACKUP) |  | 2126290 | 2185460 | 2185790 | 330 | 59500
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 99940770 | 100701840 | 761070 | 7599930
(BACKUP) |  | 93082960 | 99919890 | 100680730 | 760840 | 7597770
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4416640 | 4474410 | 57770 | 332180
(BACKUP) |  | 4144060 | 4418560 | 4476340 | 57780 | 332280
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 108764365 | 109592162 | 827797 | 8268907
TOTAL |  |  |  |  | 827797 | 8268907
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 17757678 | 17930013 | 172335 | 1399758
TOTAL |  |  |  |  | 172335 | 1399758
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3254168.8 | 3272375.81 | 18207.01 | 183057.47
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1044405.59 | 1049851.96 | 5446.37 | 60093.55
U Ijen 5 |  | 7258.6 | 7650.1 | 7693.6 | 43.5 | 435
U Ijen 6 |  | 247889 | 259769 | 261121 | 1352 | 13232
U Ijen 8 |  | 299837 | 314257 | 315788 | 1531 | 15951
TOTAL |  |  |  |  | 26579.88 | 272769.02
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-10 01:00 | 34.9589 | 6.4124 | 0.88654 | 0.92561 | 18.5182 | 1.9234 | 12.7444 | 193.1204 | 18.0535 | 192.2654 | 20.0816 | 38.0517 | 14.411 | 199.4762 | 23.4247 | 37.9959 | 14.2095 | 197.2502 | 21.4482 | 34.9116 | 14.2956 | 197.0896 | 20.6341 | 39.5288 | 14.288 | 198.4103 | 195.4219 | 13.3765 | 54.2143 | 2.1642 | 9.9691 | 0 | 75.877 | 21.897 | 47.5759 | 13.4816 | 191.2943 | 194.7144 | 13.1272 | 2.9593 | 61.0806 | 6.1601 | 67.2408 | 15.0962 | 132.5454 | 124.7683 | 99.9584 | 15.0703 | 18.0535 | 192.2654 | 121.9059 | 15.054 | 1.2361 | 38.7869 | 75.8313 | 0.35875 | 0.13783 | 0.069958 | 19.1753 | 0.76018 | 0.34229
2025-06-10 02:00 | 34.9994 | 5.8238 | 0.89039 | 0.93181 | 18.5567 | 1.8825 | 12.7371 | 193.1024 | 18.051 | 192.1922 | 20.0031 | 38.0547 | 14.3995 | 199.4498 | 23.1439 | 37.9954 | 14.1953 | 197.2262 | 21.411 | 35.0195 | 14.2855 | 197.1161 | 20.6867 | 40.0199 | 14.2933 | 198.4765 | 195.414 | 13.372 | 54.1871 | 2.1085 | 9.9702 | 0 | 75.8164 | 21.8609 | 49.0099 | 13.4923 | 191.358 | 194.7145 | 13.1247 | 3.0136 | 60.304 | 5.5836 | 65.8876 | 15.093 | 132.6544 | 124.6647 | 99.96 | 15.0667 | 18.051 | 192.1922 | 121.7452 | 15.051 | 1.2386 | 38.8332 | 75.4405 | 0.3589 | 0.13745 | 0.069944 | 19.5429 | 0.76018 | 0.34265
2025-06-10 03:00 | 34.7191 | 5.9641 | 0.87815 | 0.92192 | 18.6216 | 1.903 | 12.6418 | 192.7824 | 17.9298 | 192.3235 | 19.9295 | 38.0566 | 14.2843 | 199.0867 | 22.3776 | 37.9963 | 14.0657 | 196.8166 | 20.9993 | 35.0198 | 14.1594 | 196.7474 | 20.7157 | 40.0164 | 14.1872 | 198.3061 | 195.0698 | 13.266 | 53.5461 | 2.0624 | 9.9675 | 0 | 75.7728 | 21.7967 | 49.0245 | 13.4081 | 191.1566 | 194.4039 | 13.029 | 3.086 | 59.5031 | 6.5663 | 66.0694 | 14.9932 | 131.8699 | 124.5764 | 99.9612 | 14.9674 | 17.9298 | 192.3235 | 121.84 | 14.9297 | 1.2336 | 38.5454 | 75.7916 | 0.10727 | 0.13379 | 0.070294 | 18.3363 | 0.75134 | 0.34418
2025-06-10 04:00 | 34.5416 | 6.6244 | 0.89056 | 0.92421 | 18.5792 | 1.9592 | 12.5498 | 192.4604 | 17.8425 | 192.1292 | 19.8296 | 38.0564 | 14.1858 | 198.7845 | 22.1239 | 38.3417 | 13.9692 | 196.4312 | 20.9743 | 35.0209 | 14.0675 | 196.4725 | 20.6306 | 40.0193 | 14.0943 | 198.0605 | 194.7398 | 13.1679 | 53.3856 | 2.0473 | 9.9688 | 0 | 75.7152 | 21.7385 | 50.1785 | 13.3275 | 190.9197 | 194.1014 | 12.9404 | 3.1053 | 60.7298 | 6.9427 | 67.6725 | 14.9216 | 131.416 | 124.5528 | 99.9603 | 14.8963 | 17.8425 | 192.1292 | 121.8684 | 14.8428 | 1.2323 | 38.309 | 76.2612 | 0.10716 | 0.13702 | 0.070243 | 18.1393 | 0.75114 | 0.3433
2025-06-10 05:00 | 34.5928 | 7.4467 | 0.87807 | 0.91538 | 18.2742 | 1.9434 | 12.5598 | 192.5002 | 17.8598 | 192.0378 | 19.7637 | 38.058 | 14.1895 | 198.8049 | 21.9628 | 38.5841 | 13.9749 | 196.4314 | 21.3122 | 35.0223 | 14.0833 | 196.5257 | 20.5746 | 40.0212 | 14.1025 | 198.0915 | 194.7744 | 13.1765 | 53.3788 | 2.051 | 9.9716 | 0 | 75.6567 | 21.6657 | 50.1794 | 13.3298 | 190.924 | 194.1339 | 12.9488 | 3.0811 | 60.3037 | 6.9246 | 67.2283 | 14.937 | 131.532 | 124.6083 | 99.9598 | 14.9115 | 17.8598 | 192.0378 | 121.685 | 14.8601 | 1.2349 | 38.3438 | 76.1455 | 0.17179 | 0.13938 | 0.070132 | 18.5847 | 0.75647 | 0.34071
2025-06-10 06:00 | 34.5407 | 7.26 | 0.86255 | 0.90772 | 18.2764 | 1.8915 | 12.5693 | 192.5205 | 17.8604 | 192.0956 | 19.7232 | 37.9174 | 14.1848 | 198.778 | 21.8069 | 38.1618 | 13.9653 | 196.42 | 21.3688 | 35.0674 | 14.0771 | 196.4862 | 20.5735 | 40.023 | 14.1029 | 198.0755 | 194.7817 | 13.1831 | 53.1829 | 2.1088 | 9.973 | 0 | 75.6311 | 21.643 | 50.1883 | 13.3366 | 190.9095 | 194.1421 | 12.9561 | 3.3013 | 58.0723 | 7.2608 | 65.3331 | 14.9317 | 131.8308 | 124.4387 | 99.9613 | 14.9062 | 17.8604 | 192.0956 | 121.468 | 14.8603 | 1.2302 | 38.4125 | 75.9184 | 0.17231 | 0.13502 | 0.070808 | 18.2128 | 0.75237 | 0.34782
2025-06-10 07:00 | 34.3435 | 6.5511 | 0.86945 | 0.91372 | 18.513 | 1.7593 | 12.5354 | 192.4107 | 17.8116 | 192.0778 | 19.7666 | 37.4278 | 14.1373 | 198.6179 | 21.6122 | 38.2857 | 13.9079 | 196.2569 | 21.0951 | 35.5558 | 14.0158 | 196.3418 | 20.5769 | 40.027 | 14.059 | 197.9448 | 194.6603 | 13.1454 | 52.933 | 2.2847 | 9.976 | 0 | 75.6653 | 21.6388 | 50.8107 | 13.3262 | 190.9011 | 194.0377 | 12.9246 | 3.3557 | 52.8024 | 7.6191 | 60.4215 | 14.8904 | 131.8233 | 124.2659 | 99.9646 | 14.8659 | 17.8116 | 192.0778 | 121.5648 | 14.8115 | 1.1986 | 38.3252 | 76.1192 | 0.10911 | 0.1234 | 0.072565 | 17.8746 | 0.73425 | 0.35477
2025-06-10 08:00 | 34.1552 | 7.1797 | 0.88647 | 0.93164 | 19.1381 | 1.6504 | 12.5218 | 192.3669 | 17.7993 | 192.0775 | 19.8325 | 37.0819 | 14.1385 | 198.5554 | 21.4957 | 38.7735 | 13.8963 | 196.2086 | 21.2714 | 35.9955 | 14.0036 | 196.3159 | 20.5802 | 40.0376 | 14.051 | 197.9135 | 194.6078 | 13.1312 | 52.6796 | 2.3619 | 9.9746 | 0 | 75.7735 | 21.5969 | 51.8084 | 13.3478 | 190.9838 | 194.0177 | 12.917 | 3.2575 | 48.7475 | 7.6237 | 56.3712 | 14.8874 | 131.8418 | 124.3905 | 99.9691 | 14.8648 | 17.7993 | 192.0775 | 121.9008 | 14.8003 | 1.1464 | 38.3124 | 76.6928 | 0.70268 | 0.11298 | 0.074704 | 17.8834 | 0.69662 | 0.35375
2025-06-10 09:00 | 34.02 | 8.3075 | 0.91811 | 0.96517 | 20.0995 | 1.6705 | 12.5207 | 192.3545 | 17.806 | 192.0694 | 19.8202 | 37.0848 | 14.1502 | 198.5483 | 20.1586 | 38.8231 | 13.9018 | 196.2205 | 21.4286 | 36.2631 | 14.0012 | 196.2867 | 20.4931 | 39.985 | 14.0441 | 197.8381 | 194.6127 | 13.1369 | 52.7852 | 2.3096 | 9.9738 | 0 | 75.907 | 21.4529 | 52.7119 | 13.3531 | 191.0179 | 194.0127 | 12.9169 | 3.3086 | 49.2869 | 7.5429 | 56.8297 | 14.8963 | 131.7619 | 124.7117 | 99.9717 | 14.8754 | 17.806 | 192.0694 | 122.2918 | 14.8067 | 1.1096 | 38.1877 | 77.4357 | 0.75497 | 0.11105 | 0.076357 | 17.9611 | 0.65753 | 0.35295
2025-06-10 10:00 | 33.6219 | 8.6208 | 0.92075 | 0.96883 | 20.3494 | 1.7805 | 12.527 | 192.3634 | 17.787 | 192.0197 | 19.894 | 37.6433 | 14.1985 | 198.6163 | 19.5282 | 39.2124 | 13.9493 | 196.3397 | 21.1567 | 38.9633 | 14.1019 | 196.619 | 20.4744 | 41.0705 | 14.11 | 197.9135 | 194.5822 | 13.1336 | 51.4747 | 2.3008 | 9.977 | 0 | 76.0457 | 21.3206 | 53.6836 | 13.349 | 191.0161 | 194.0103 | 12.9165 | 3.3287 | 51.4886 | 8.3765 | 59.8652 | 14.9304 | 131.6969 | 124.9136 | 99.9723 | 14.91 | 17.787 | 192.0197 | 122.9223 | 14.7873 | 1.101 | 38.2206 | 78.4693 | 9.4526 | 0.11166 | 0.076965 | 17.3721 | 0.63437 | 0.34947
2025-06-10 11:00 | 33.8201 | 7.3564 | 0.9153 | 0.9676 | 20.185 | 1.8951 | 12.5793 | 192.5322 | 17.8401 | 191.9821 | 20.5155 | 39.1444 | 14.3607 | 199.0611 | 20.6033 | 39.803 | 14.0852 | 196.7181 | 20.8198 | 41.3604 | 14.2855 | 197.1339 | 20.5766 | 42.3874 | 14.2749 | 198.4808 | 194.7423 | 9.5364 | 51.6987 | 2.301 | 9.9791 | 0 | 76.1289 | 21.2725 | 54.1381 | 13.3945 | 191.1286 | 194.1743 | 12.9682 | 3.206 | 55.7108 | 8.3806 | 64.0914 | 15.0452 | 132.0144 | 125.153 | 99.9708 | 15.0237 | 17.8401 | 191.9821 | 122.5022 | 14.8403 | 1.1239 | 38.422 | 77.811 | 18.0091 | 0.11092 | 0.076058 | 17.6083 | 0.64509 | 0.34472
2025-06-10 12:00 | 34.4326 | 6.9204 | 0.92722 | 0.98441 | 20.374 | 1.8918 | 12.6065 | 192.6329 | 17.8999 | 192.0225 | 21.4424 | 40.0882 | 14.4971 | 199.4785 | 20.8358 | 40.0035 | 14.1682 | 197.0073 | 20.3175 | 42.1858 | 14.351 | 197.2706 | 20.3341 | 42.8188 | 14.3488 | 198.8452 | 194.9134 | 4.4949 | 53.5762 | 2.4724 | 9.9799 | 0 | 76.1809 | 21.2554 | 54.1428 | 13.4227 | 191.2162 | 194.2843 | 12.9996 | 3.1079 | 58.3999 | 6.7412 | 65.1411 | 15.1084 | 132.4466 | 124.9228 | 99.9698 | 15.0869 | 17.8999 | 192.0225 | 122.0653 | 14.8999 | 1.1237 | 38.6291 | 76.8514 | 16.9491 | 0.11069 | 0.076873 | 19.0319 | 0.64545 | 0.34309
2025-06-10 13:00 | 34.4234 | 7.7408 | 0.94863 | 1.0035 | 20.7649 | 1.8664 | 12.5983 | 192.5974 | 17.9049 | 192.0305 | 21.9616 | 40.0873 | 14.5463 | 199.5833 | 20.9644 | 39.9982 | 14.1904 | 197.0652 | 19.9426 | 43.0473 | 14.3631 | 197.278 | 20.0566 | 43.0787 | 14.3506 | 198.787 | 194.9067 | 3.4673 | 53.919 | 2.8536 | 9.9819 | 0 | 76.2882 | 21.2631 | 54.133 | 13.4178 | 191.1954 | 194.2608 | 12.9917 | 3.1547 | 58.3575 | 5.8893 | 64.2468 | 15.1092 | 132.6024 | 124.5973 | 99.9707 | 15.0886 | 17.9049 | 192.0305 | 122.6191 | 14.905 | 1.0956 | 38.8499 | 77.275 | 16.3024 | 0.11096 | 0.079218 | 19.6186 | 0.6172 | 0.34484
2025-06-10 14:00 | 34.3351 | 7.7657 | 0.9595 | 1.0135 | 21.0028 | 1.8533 | 12.6166 | 192.6537 | 17.926 | 191.9891 | 22.1475 | 40.0869 | 14.5722 | 199.6479 | 20.9895 | 39.9996 | 14.2082 | 197.0653 | 19.7576 | 43.0478 | 14.3802 | 197.281 | 20.0363 | 43.081 | 14.3552 | 198.7219 | 194.9626 | 5.2936 | 54.0115 | 3.2354 | 9.984 | 0 | 76.3852 | 21.2641 | 54.018 | 13.4351 | 191.2493 | 194.3157 | 13.0085 | 3.2138 | 57.7967 | 5.8378 | 63.6345 | 15.1398 | 132.4108 | 125.0349 | 99.9717 | 15.1201 | 17.926 | 191.9891 | 123.0304 | 14.9259 | 1.1042 | 38.7886 | 77.8424 | 15.842 | 0.11042 | 0.079598 | 19.7477 | 0.6048 | 0.3451
2025-06-10 15:00 | 34.4556 | 6.8743 | 0.94525 | 0.99316 | 20.5748 | 1.8748 | 12.6809 | 192.8707 | 17.9832 | 192.0268 | 22.2278 | 40.0921 | 14.616 | 199.8116 | 20.9244 | 39.9989 | 14.2514 | 197.2122 | 19.6899 | 42.91 | 14.4342 | 197.3907 | 20.0111 | 43.0745 | 14.3958 | 198.7954 | 195.171 | 9.7676 | 53.8805 | 3.5083 | 9.9799 | 0 | 76.3927 | 21.2416 | 53.0411 | 13.4844 | 191.3914 | 194.5205 | 13.0692 | 3.3321 | 58.3903 | 6.2082 | 64.5986 | 15.1932 | 132.3592 | 125.2375 | 99.9696 | 15.1724 | 17.9832 | 192.0268 | 122.9778 | 14.9834 | 1.1435 | 38.8175 | 77.7155 | 14.9134 | 0.11131 | 0.076943 | 19.535 | 0.7637 | 0.33972
2025-06-10 16:00 | 34.5348 | 5.3755 | 0.91958 | 0.96112 | 19.7342 | 1.9531 | 12.7113 | 192.9803 | 18.0036 | 192.1309 | 22.2098 | 40.101 | 14.5881 | 199.8483 | 20.8757 | 39.9931 | 14.2397 | 197.224 | 19.6157 | 41.8915 | 14.425 | 197.3348 | 19.9616 | 43.0622 | 14.3929 | 198.6743 | 195.261 | 13.0533 | 53.7275 | 3.5931 | 9.9754 | 0 | 76.2761 | 21.2186 | 52.2731 | 13.5055 | 191.4765 | 194.6293 | 13.1006 | 3.4476 | 60.542 | 6.908 | 67.4501 | 15.2027 | 132.2295 | 124.979 | 99.9629 | 15.1787 | 18.0036 | 192.1309 | 122.2515 | 15.0038 | 1.1904 | 38.8678 | 76.3796 | 13.7579 | 0.12165 | 0.072803 | 18.8859 | 0.87042 | 0.34106
2025-06-10 17:00 | 34.4559 | 6.9863 | 0.90694 | 0.94587 | 19.3228 | 1.978 | 12.6728 | 192.855 | 17.9618 | 192.2487 | 22.1774 | 40.1045 | 14.5135 | 199.7022 | 20.859 | 39.9845 | 14.176 | 197.0098 | 19.5621 | 41.0105 | 14.3609 | 197.1397 | 19.9421 | 43.0607 | 14.3383 | 198.4467 | 195.1104 | 13.2534 | 54.0004 | 3.6693 | 9.9722 | 0 | 76.1088 | 21.1929 | 53.0834 | 13.4715 | 191.3736 | 194.5163 | 13.0654 | 3.384 | 61.2246 | 6.9293 | 68.1539 | 15.154 | 132.2754 | 124.5033 | 99.9594 | 15.1287 | 17.9618 | 192.2487 | 121.8371 | 14.9615 | 1.2141 | 38.8985 | 75.573 | 13.9914 | 0.13142 | 0.070731 | 18.5546 | 0.81509 | 0.34706
2025-06-10 18:00 | 34.5274 | 8.7179 | 0.90628 | 0.9468 | 19.264 | 1.9616 | 12.7182 | 193.0088 | 18.0063 | 192.2574 | 22.1809 | 40.1041 | 14.5628 | 199.8556 | 20.8835 | 39.9785 | 14.2273 | 197.1431 | 19.8165 | 41.0129 | 14.4214 | 197.3387 | 19.9415 | 43.065 | 14.3892 | 198.6158 | 195.2706 | 13.3055 | 54.9846 | 3.7472 | 9.9741 | 0 | 75.9663 | 21.16 | 52.4049 | 13.4965 | 191.3637 | 194.6532 | 13.1068 | 3.374 | 60.338 | 7.3914 | 67.7294 | 15.1802 | 132.675 | 124.3298 | 99.9594 | 15.1543 | 18.0063 | 192.2574 | 121.8366 | 15.0059 | 1.2149 | 39.1611 | 75.3253 | 13.6955 | 0.13104 | 0.070513 | 18.5055 | 0.95299 | 0.34788
2025-06-10 19:00 | 34.5738 | 8.3451 | 0.90526 | 0.95061 | 19.1951 | 1.9527 | 12.7724 | 193.1997 | 18.0629 | 192.2933 | 22.1998 | 40.1046 | 14.6183 | 200.0297 | 20.9112 | 39.9751 | 14.2815 | 197.3145 | 19.8908 | 41.0149 | 14.4761 | 197.5019 | 19.9015 | 43.0658 | 14.4403 | 198.7823 | 195.4787 | 13.3678 | 55.4433 | 3.7433 | 9.9772 | 0 | 75.8575 | 21.186 | 51.6442 | 13.5382 | 191.4613 | 194.8324 | 13.1585 | 3.4228 | 59.9124 | 7.5998 | 67.5122 | 15.2283 | 132.7306 | 124.5242 | 99.9596 | 15.2022 | 18.0629 | 192.2933 | 121.9815 | 15.0625 | 1.2139 | 39.3414 | 75.1193 | 12.6035 | 0.13098 | 0.070599 | 18.8659 | 0.93876 | 0.34712
2025-06-10 20:00 | 34.601 | 7.7603 | 0.90227 | 0.94684 | 19.0265 | 1.9523 | 12.7372 | 193.0741 | 18.0319 | 192.3427 | 22.2117 | 40.1055 | 14.5803 | 199.9138 | 20.9199 | 39.9734 | 14.241 | 197.19 | 19.7509 | 40.9645 | 14.4317 | 197.3149 | 19.8932 | 43.0639 | 14.4007 | 198.6479 | 195.3419 | 13.3283 | 55.2425 | 3.7207 | 9.9752 | 0 | 75.7625 | 21.2198 | 52.9554 | 13.5213 | 191.4149 | 194.724 | 13.1275 | 3.2002 | 60.3254 | 7.2258 | 67.5512 | 15.2035 | 132.3866 | 124.437 | 99.96 | 15.1775 | 18.0319 | 192.3427 | 121.8342 | 15.0315 | 1.2159 | 39.2778 | 74.9973 | 12.8671 | 0.13263 | 0.070548 | 19.0269 | 0.76268 | 0.34518
2025-06-10 21:00 | 34.5321 | 6.4723 | 0.89685 | 0.9374 | 18.7467 | 1.9895 | 12.6794 | 192.8903 | 17.9768 | 192.2673 | 22.2061 | 40.1056 | 14.5212 | 199.7463 | 20.9481 | 39.9733 | 14.1811 | 197.022 | 19.8037 | 40.4579 | 14.3706 | 197.1267 | 19.9035 | 42.8393 | 14.3384 | 198.4792 | 195.1487 | 13.2673 | 54.4207 | 3.6028 | 9.9687 | 0 | 75.6642 | 21.1864 | 53.2959 | 13.4692 | 191.2876 | 194.5435 | 13.0716 | 3.1066 | 61.6273 | 7.0727 | 68.7001 | 15.1583 | 132.2333 | 124.324 | 99.9597 | 15.1321 | 17.9768 | 192.2673 | 122.2038 | 14.9768 | 1.2196 | 39.2448 | 75.5926 | 12.9286 | 0.13593 | 0.070267 | 18.6571 | 0.73857 | 0.34367
2025-06-10 22:00 | 34.3448 | 6.6352 | 0.88957 | 0.92874 | 18.5227 | 1.9802 | 12.6253 | 192.7162 | 17.9198 | 192.2415 | 22.1967 | 40.1432 | 14.4582 | 199.5601 | 20.9953 | 39.9722 | 14.1149 | 196.822 | 19.7952 | 40.0064 | 14.3011 | 196.9291 | 19.8655 | 42.3442 | 14.2658 | 198.3106 | 194.9613 | 13.2089 | 53.0861 | 3.5526 | 9.966 | 0 | 75.5816 | 21.1558 | 53.5959 | 13.4147 | 191.1428 | 194.3679 | 13.0174 | 3.1532 | 60.8972 | 7.1136 | 68.0107 | 15.1232 | 131.8067 | 124.8719 | 99.9586 | 15.0973 | 17.9198 | 192.2415 | 122.4393 | 14.9198 | 1.2165 | 38.9158 | 76.2993 | 12.7403 | 0.13869 | 0.070087 | 18.5153 | 0.73599 | 0.34388
2025-06-10 23:00 | 34.4366 | 7.1716 | 0.8865 | 0.9269 | 18.3645 | 1.9159 | 12.6396 | 192.7552 | 17.9325 | 192.1263 | 22.1676 | 40.2212 | 14.4754 | 199.6059 | 21.0298 | 39.9718 | 14.1273 | 196.8311 | 19.8689 | 40.0098 | 14.3165 | 196.9837 | 19.8899 | 42.0729 | 14.2755 | 198.2944 | 194.9956 | 13.2227 | 52.5108 | 3.7096 | 9.9698 | 0 | 75.5074 | 21.1466 | 54.8907 | 13.4454 | 191.2029 | 194.4303 | 13.037 | 3.2793 | 59.1618 | 6.8135 | 65.9753 | 15.1321 | 131.7982 | 124.9625 | 99.9577 | 15.1064 | 17.9325 | 192.1263 | 121.9978 | 14.9323 | 1.2095 | 38.8574 | 76.0387 | 13.4984 | 0.13917 | 0.070197 | 18.2402 | 0.7294 | 0.34524
2025-06-11 | 34.1566 | 5.749 | 0.89538 | 0.92609 | 18.1768 | 2.2535 | 12.4855 | 192.3152 | 17.6485 | 191.0279 | 22.0961 | 40.0658 | 14.3011 | 199.1592 | 18.6943 | 39.9718 | 13.9062 | 196.3872 | 20.0241 | 40.0104 | 14.1414 | 196.6516 | 19.8957 | 42.0715 | 14.0904 | 197.8693 | 194.6217 | 13.0638 | 51.0075 | 3.9477 | 9.9634 | 0 | 75.4269 | 21.2376 | 51.3559 | 13.2232 | 190.8644 | 193.9474 | 12.8659 | 2.9999 | 66.3029 | 10.6683 | 76.9713 | 14.9409 | 130.2977 | 125.2814 | 99.9588 | 14.9159 | 17.6485 | 191.0279 | 122.0158 | 14.6496 | 1.2021 | 37.8569 | 75.442 | 15.7048 | 0.13658 | 0.070491 | 10.2556 | 0.72205 | 0.34279
Total | MW: 826.1225; MVAR: 170.0615; kg/s: 4619795.6211; kg/s: 277843.8845; kg/s: 5044700.262; kg/s: 616968.6779; kg/s: 5661668.9399; kg/s: 11409258.8492
Average | 34.4218 | 7.0859 | 0.90357 | 0.94744 | 19.2575 | 1.9034 | 12.6263 | 192.711 | 17.9125 | 192.0948 | 21.1077 | 39.0828 | 14.3955 | 199.3217 | 21.1695 | 39.3236 | 14.1014 | 196.8172 | 20.4634 | 38.9904 | 14.2562 | 196.9448 | 20.2562 | 41.6598 | 14.2496 | 198.3659 | 194.9813 | 11.8217 | 53.4699 | 2.894 | 9.9737 | 0 | 75.8912 | 21.4005 | 52.0893 | 13.4163 | 191.1771 | 194.3537 | 13.0162 | 3.2158 | 58.3877 | 7.1408 | 65.5286 | 15.0623 | 132.0516 | 124.7104 | 99.9636 | 15.0383 | 17.9125 | 192.0948 | 122.116 | 14.9126 | 1.1854 | 38.6752 | 76.3487 | 9.0041 | 0.12633 | 0.072787 | 18.2555 | 0.74153 | 0.34555
Min | 33.6219 | 5.3755 | 0.86255 | 0.90772 | 18.1768 | 1.6504 | 12.4855 | 192.3152 | 17.6485 | 191.0279 | 19.7232 | 37.0819 | 14.1373 | 198.5483 | 18.6943 | 37.9954 | 13.8963 | 196.2086 | 19.5621 | 34.9116 | 14.0012 | 196.2867 | 19.8655 | 39.5288 | 14.0441 | 197.8381 | 194.5822 | 3.4673 | 51.0075 | 2.0473 | 9.9634 | 0 | 75.4269 | 21.1466 | 47.5759 | 13.2232 | 190.8644 | 193.9474 | 12.8659 | 2.9593 | 48.7475 | 5.5836 | 56.3712 | 14.8874 | 130.2977 | 124.2659 | 99.9577 | 14.8648 | 17.6485 | 191.0279 | 121.468 | 14.6496 | 1.0956 | 37.8569 | 74.9973 | 0.10716 | 0.11042 | 0.069944 | 10.2556 | 0.6048 | 0.33972
Max | 34.9994 | 8.7179 | 0.9595 | 1.0135 | 21.0028 | 2.2535 | 12.7724 | 193.1997 | 18.0629 | 192.3427 | 22.2278 | 40.2212 | 14.6183 | 200.0297 | 23.4247 | 40.0035 | 14.2815 | 197.3145 | 21.4482 | 43.0478 | 14.4761 | 197.5019 | 20.7157 | 43.081 | 14.4403 | 198.8452 | 195.4787 | 13.3765 | 55.4433 | 3.9477 | 9.984 | 0 | 76.3927 | 21.897 | 54.8907 | 13.5382 | 191.4765 | 194.8324 | 13.1585 | 3.4476 | 66.3029 | 10.6683 | 76.9713 | 15.2283 | 132.7306 | 125.2814 | 99.9723 | 15.2022 | 18.0629 | 192.3427 | 123.0304 | 15.0625 | 1.2386 | 39.3414 | 78.4693 | 18.0091 | 0.13938 | 0.079598 | 19.7477 | 0.95299 | 0.35477

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1
18 |  | Night | 22:15 | 5.55 | 22.2
19 | 2025-06-10 | Day | 8:55 | 5.69 | 31.6
20 |  | Night | 0:20 | 5.18 | 24.3
21 | 2025-06-11 | Day
22 |  | Night
23 | 2025-06-12 | Day
24 |  | Night
25 | 2025-06-13 | Day
26 |  | Night
27 | 2025-06-14 | Day
28 |  | Night
29 | 2025-06-15 | Day
30 |  | Night
31 | 2025-06-16 | Day
32 |  | Night
33 | 2025-06-17 | Day
34 |  | Night
35 | 2025-06-18 | Day
36 |  | Night
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-10
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0