## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-11
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 20.0644 | 199.2488 | 39.7756
|  | #6-2 | Production | 21.5431 | 196.9009 | 40.4757
|  | #6-3 | Production | 20.6958 | 196.7817 | 35.5934
|  | #6-4 | Production | 20.0677 | 198.362 | 41.5992
|  | #8-1 | Shut in | 4.7677 | 75.237 | 9.974
|  | #8-2 | Production | 20.8545 | 191.2048 | 56.2872
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 53.4169 | 4615217.171
|  | PAD #8 - STEAM |  |  |  |  | 3.275 | 282957.6797 | Online
|  | BRINE HEADER |  |  |  |  | 5.8874 | 508670.4838 | Offline
|  | TOTAL FLOW |  |  |  |  | 62.5792 | 5406845.3346
|  | PRESS SEPARATOR IJN 6 | Online | 12.5239 | 195.0487
|  | PRESS SEPARATOR IJN 8 | Online | 13.0425 | 194.4365
| INJECTION WELL | #5-1 | Injection | 15.1265 | 124.8941 | 99.9627 | 132.121 | 11415254.1084
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.6223 |  |  | 830.9346
|  | NET | 31.8662 |  |  | 764.7879
| PARASITIC LOAD |  | 2.7561 |  |  | 66.1467
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 1.8075 |  |  | 6506.9447
|  | NET | 1.9638 |  |  | 7069.7317
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-11
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 764787.9101 |  | 0 |  | 764787.9101
|  |  |  | 764787.9101 |  | 0 |  | 764787.9101
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 765310 | [7 empty] | 765310
M-T-D GROSS GENERATION (kWHR) |  |  |  | 9100461 | [7 empty] | 9100461
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18215.91 | 0 | 4961.58 | 42.7 | 1515 | 1392 | 26127.19
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 201273.38 | -283254.3 | 65055.13 | 477.7 | 14747 | 17343 | 97622.83
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.6223 |  |  | 6.3311 |  | 18.6949
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 264
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 92.38%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 4615.2172 |  | 282.9577 |  |  | 5242.529
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.053417 |  | 0.003275 |  |  | 0.060677
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 508.6705
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.0058874
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 5751.1995
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.066565
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 192.7723 |  |  |  | 191.7568
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.6457 |  |  |  | 17.9486
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 16.2402 |  | 21.1495 |  |  | 18.6949
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [14 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [13 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:01 | PLN adviced load ROH 31.72 MW (Mr. Eko Safii)
0:48 | Stop electrical pit pump IJN-6 (Level pond : 54.1%)
0:49 | Start pit pump IJN 8 (Level pond : 38.8%)
3:48 | Stop pit pump IJN 8 (Level pond : 32.5%)
3:49 | Start electrical pit pump IJN-6 (Level pond : 61.7%)
6:52 | Stop electrical pit pump IJN-6 (Level pond : 53.1%)
6:53 | Start pit pump IJN 8 (Level pond : 36.5%)
10:00 | Stop pit pump IJN-8 (Level pond : 30.1%)
10:20 | Dismantle scalling coupon by SOLENIS on IJN-5
10:59 | Start electrical pit pump IJN-6 (Level pond : 54.8%)
11:21 | Eyewash inspection (Standard Activities)
11:34 | Drain strainer-A suction brine booster pump IJN-6--> Result : There is passing on valve (Standard Activity)
11:45 | Drain strainer-A suction brine booster pump IJN-8--> Result : No passing (Standard Activity)
12:04 | Take a NCG sampling at NCG Valve CCW Side --> Opening at 16% around 20 minutes for take sampling
12:57 | Running test air compressor-B due to check abnormally on bearing by IKPT Team
13:50 | Stop electrical pit pump IJN-6 (Level pond : 47.3%)
13:57 | Cleaning PT-2208 (Pressure outlet separator IJN-6) due to blockage indication
14:01 | Can't Cleaning WHP 6-2 PT-2006B due to valve manifold passing resulting delay reading the value
15:00 | Tightening flange on lube oil return turbine CW side & add seal tape by mechanical maintenance team
16:06 | Changeover service water pump from B to A (Standard Activities)
16:10 | Changover again from service water pump A to B due to low pressure (Discharge Pressure : 1.8 Bar)
16:29 | Start electrical pit pump IJN-6 (Level pond : 48.2%)
16:40 | Exercise master valve IJN 8.2 (Standard Activity)
17:00 | Update pH brine+condensate inlet preheater (pH : 5.07 and Temperature : 21.6 degC)
19:11 | Stop electrical pit pump IJN-6 (level pond : 42.3%)
20:07 | Start pit pump IJN 8 (Level pond : 43.7%) with pressure 21.7bar and current 125A
21:24 | Stop pit pump IJN 8 (Level pond : 42.8%)
21:25 | Start electrical pit pump IJN-6 (Level pond : 41.3%) with pressure 17.8bar and current 92A
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Arbima |  |  |  | CCR Operator : Dwiki |  |  |  | Steamfield : Vandy
Night Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Tio |  |  |  | Steamfield : Rafly
22
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-11
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2187420 | 2188250 | 830 | 60400
(BACKUP) |  | 2126290 | 2185790 | 2186620 | 830 | 60330
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 100701840 | 101467150 | 765310 | 8365240
(BACKUP) |  | 93082960 | 100680730 | 101445830 | 765100 | 8362870
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4474410 | 4512310 | 37900 | 370080
(BACKUP) |  | 4144060 | 4476340 | 4514260 | 37920 | 370200
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 109592162 | 110423716 | 831554 | 9100461
TOTAL |  |  |  |  | 831554 | 9100461
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 17930013 | 18082581 | 152568 | 1552326
TOTAL |  |  |  |  | 152568 | 1552326
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3272375.81 | 3290591.72 | 18215.91 | 201273.38
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1049851.96 | 1054813.54 | 4961.58 | 65055.13
U Ijen 5 |  | 7258.6 | 7693.6 | 7736.3 | 42.7 | 477.7
U Ijen 6 |  | 247889 | 261121 | 262636 | 1515 | 14747
U Ijen 8 |  | 299837 | 315788 | 317180 | 1392 | 17343
TOTAL |  |  |  |  | 26127.19 | 298896.21
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-11 01:00 | 34.232 | 5.9875 | 0.88766 | 0.92705 | 18.2261 | 1.9596 | 12.5978 | 192.6146 | 17.8726 | 192.0449 | 22.2284 | 40.0541 | 14.4336 | 199.4737 | 21.0599 | 39.9699 | 14.0826 | 196.7176 | 19.8751 | 39.4539 | 14.269 | 196.934 | 20.0139 | 42.0739 | 14.2393 | 198.2485 | 194.8209 | 13.1701 | 52.1967 | 3.95 | 9.9654 | 0 | 75.3282 | 20.9107 | 57.9415 | 13.3924 | 191.0387 | 194.2967 | 12.996 | 3.2106 | 59.5633 | 7.5172 | 67.0805 | 15.0654 | 131.9686 | 124.108 | 99.9589 | 15.0392 | 17.8726 | 192.0449 | 121.6852 | 14.8726 | 1.2075 | 38.9851 | 75.3643 | 16.3632 | 0.1397 | 0.070172 | 17.5176 | 0.72662 | 0.34481
2025-06-11 02:00 | 34.4868 | 5.8235 | 0.89222 | 0.93101 | 18.2254 | 1.9003 | 12.685 | 192.906 | 17.9679 | 191.5881 | 22.1372 | 40.0529 | 14.5124 | 199.7389 | 21.1425 | 39.9679 | 14.1535 | 196.9397 | 19.8265 | 38.5383 | 14.3225 | 197.1192 | 20.0903 | 41.6014 | 14.3039 | 198.4992 | 195.1599 | 13.2763 | 52.6894 | 3.9855 | 9.9668 | 0 | 75.2361 | 20.8924 | 55.0765 | 13.458 | 191.2318 | 194.571 | 13.0796 | 3.2382 | 58.9466 | 6.5887 | 65.5353 | 15.1425 | 132.4018 | 124.28 | 99.9581 | 15.1162 | 17.9679 | 191.5881 | 122.4772 | 14.9678 | 1.213 | 39.3165 | 75.9835 | 11.6307 | 0.14302 | 0.070039 | 17.4999 | 0.89605 | 0.34301
2025-06-11 03:00 | 35.0404 | 5.7055 | 0.88777 | 0.92523 | 18.22 | 1.8554 | 12.7079 | 192.9831 | 18.0074 | 191.483 | 21.2227 | 40.051 | 14.4848 | 199.6987 | 21.2117 | 39.9675 | 14.1418 | 196.9198 | 19.7882 | 37.4341 | 14.2853 | 197.0328 | 19.937 | 41.5799 | 14.2911 | 198.5197 | 195.2993 | 13.3194 | 53.6494 | 4.0711 | 9.9694 | 0 | 75.1573 | 20.9144 | 53.7289 | 13.4787 | 191.2781 | 194.6349 | 13.1016 | 3.1922 | 59.5763 | 5.4366 | 65.0129 | 15.1947 | 132.2046 | 125.0726 | 99.9576 | 15.1686 | 18.0074 | 191.483 | 122.2701 | 15.0073 | 1.2121 | 39.1348 | 75.9225 | 2.6224 | 0.14359 | 0.070085 | 18.881 | 0.94335 | 0.34173
2025-06-11 04:00 | 35.0129 | 6.6682 | 0.86968 | 0.90759 | 17.8697 | 1.8606 | 12.6329 | 192.7365 | 17.9382 | 191.8485 | 20.2723 | 40.0465 | 14.3397 | 199.2659 | 21.265 | 39.9659 | 14.0326 | 196.6063 | 19.821 | 36.4251 | 14.1661 | 196.703 | 19.9629 | 42.0516 | 14.2032 | 198.3479 | 195.0202 | 13.233 | 53.474 | 4.0973 | 9.973 | 0 | 75.095 | 20.9538 | 56.7658 | 13.4349 | 191.1741 | 194.4196 | 13.0348 | 3.2585 | 59.4185 | 5.7272 | 65.1456 | 15.1378 | 132.0163 | 124.8682 | 99.9578 | 15.112 | 17.9382 | 191.8485 | 121.6759 | 14.9383 | 1.2071 | 38.9513 | 75.5625 | 0.85413 | 0.14583 | 0.069964 | 19.384 | 0.82282 | 0.34118
2025-06-11 05:00 | 34.9557 | 7.0558 | 0.86871 | 0.90423 | 17.5723 | 1.8585 | 12.6266 | 192.715 | 17.9412 | 191.8392 | 19.9727 | 40.0436 | 14.3105 | 199.1806 | 21.3412 | 39.963 | 14.0227 | 196.5721 | 20.1785 | 35.5857 | 14.1627 | 196.6964 | 20.1195 | 42.0706 | 14.2037 | 198.4055 | 194.9846 | 13.2242 | 53.3743 | 4.0492 | 9.9765 | 0 | 75.0224 | 20.8612 | 58.161 | 13.4276 | 191.1735 | 194.413 | 13.0319 | 3.2605 | 59.373 | 5.5912 | 64.9642 | 15.1294 | 132.19 | 124.3894 | 99.9567 | 15.1033 | 17.9412 | 191.8392 | 121.9069 | 14.9411 | 1.2125 | 39.1381 | 75.5801 | 1.6016 | 0.15311 | 0.069535 | 18.8177 | 0.82496 | 0.34218
2025-06-11 06:00 | 34.8681 | 6.8673 | 0.87817 | 0.91066 | 17.6068 | 1.8649 | 12.5975 | 192.6208 | 17.9136 | 191.7713 | 19.7725 | 40.0507 | 14.2654 | 199.0668 | 21.382 | 39.961 | 13.9952 | 196.5113 | 20.6331 | 35.0915 | 14.1343 | 196.6344 | 19.9782 | 42.0696 | 14.1732 | 198.3225 | 194.8972 | 13.1958 | 53.4953 | 4.0225 | 9.9756 | 0 | 74.9578 | 20.7386 | 58.2401 | 13.3896 | 191.0573 | 194.3032 | 13 | 3.1791 | 59.3573 | 5.6696 | 65.027 | 15.1093 | 131.8981 | 124.5212 | 99.9572 | 15.0832 | 17.9136 | 191.7713 | 121.8639 | 14.9134 | 1.214 | 39.0006 | 75.5539 | 1.4452 | 0.15353 | 0.069953 | 19.0346 | 0.82139 | 0.34985
2025-06-11 07:00 | 34.7724 | 6.6654 | 0.88791 | 0.92346 | 18.1002 | 1.8976 | 12.5721 | 192.5407 | 17.8835 | 191.6971 | 19.6025 | 40.0615 | 14.2266 | 198.9491 | 21.3986 | 39.956 | 13.9641 | 196.4466 | 20.7151 | 35.0227 | 14.0855 | 196.534 | 19.9262 | 42.066 | 14.1398 | 198.1879 | 194.8197 | 13.1709 | 53.4739 | 4.0814 | 9.976 | 0 | 74.97 | 20.7365 | 58.2431 | 13.3687 | 191.004 | 194.2131 | 12.9737 | 3.2053 | 60.2243 | 5.76 | 65.9843 | 15.0826 | 131.971 | 124.419 | 99.9618 | 15.0576 | 17.8835 | 191.6971 | 121.8744 | 14.8832 | 1.1807 | 38.941 | 75.7047 | 0.95364 | 0.13465 | 0.071798 | 19.0583 | 0.79745 | 0.357
2025-06-11 08:00 | 34.5078 | 5.8897 | 0.89822 | 0.94021 | 18.769 | 1.9519 | 12.5777 | 192.5595 | 17.8738 | 191.8325 | 19.543 | 40.0805 | 14.2361 | 198.8996 | 21.396 | 39.9515 | 13.9606 | 196.396 | 20.5974 | 35.0287 | 14.0617 | 196.4068 | 19.958 | 42.0677 | 14.1278 | 198.1144 | 194.8156 | 13.1726 | 53.2175 | 4.2412 | 9.9773 | 0 | 75.0422 | 20.7538 | 58.2479 | 13.3796 | 191.0286 | 194.2214 | 12.9759 | 3.213 | 61.063 | 6.2921 | 67.355 | 15.0786 | 132.0894 | 124.4284 | 99.9653 | 15.0554 | 17.8738 | 191.8325 | 122.1666 | 14.8737 | 1.1169 | 38.9355 | 76.2572 | 0.79279 | 0.11591 | 0.073929 | 18.6931 | 0.74927 | 0.35451
2025-06-11 09:00 | 34.2239 | 5.7347 | 0.91141 | 0.95825 | 19.4444 | 1.9803 | 12.5796 | 192.5607 | 17.8667 | 192.0015 | 19.5255 | 40.1042 | 14.2418 | 198.8697 | 21.3892 | 39.9524 | 13.9625 | 196.3409 | 20.6646 | 35.0285 | 14.0612 | 196.3291 | 19.9901 | 42.0786 | 14.1239 | 198.0864 | 194.8002 | 13.1729 | 53.0006 | 4.4212 | 9.9731 | 0 | 75.1425 | 20.765 | 58.2537 | 13.3855 | 191.0482 | 194.2207 | 12.9752 | 3.2317 | 61.283 | 6.4905 | 67.7734 | 15.0847 | 131.9192 | 124.7889 | 99.9671 | 15.0625 | 17.8667 | 192.0015 | 122.4807 | 14.8669 | 1.0726 | 38.8458 | 76.9422 | 1.3672 | 0.11107 | 0.075599 | 18.6322 | 0.69865 | 0.34903
2025-06-11 10:00 | 34.1186 | 6.0438 | 0.92533 | 0.97561 | 20.1483 | 1.9882 | 12.585 | 192.5735 | 17.8725 | 192.0234 | 19.4886 | 40.1131 | 14.2578 | 198.8861 | 21.4873 | 39.9541 | 13.9816 | 196.3607 | 20.9375 | 35.0284 | 14.0819 | 196.3974 | 20.0014 | 42.0906 | 14.1352 | 198.1074 | 194.8157 | 13.1832 | 53.0308 | 4.5588 | 9.974 | 0 | 75.2701 | 20.7723 | 58.2548 | 13.3975 | 191.0819 | 194.2332 | 12.9802 | 3.2666 | 61.3152 | 6.5186 | 67.8337 | 15.0949 | 131.797 | 125.025 | 99.9694 | 15.0732 | 17.8725 | 192.0234 | 122.7057 | 14.8728 | 1.0576 | 38.7786 | 77.6575 | 1.8413 | 0.11099 | 0.076998 | 18.683 | 0.66878 | 0.34299
2025-06-11 11:00 | 34.1425 | 6.0163 | 0.93878 | 0.99212 | 20.6322 | 1.9826 | 12.5851 | 192.5678 | 17.879 | 191.9297 | 19.4693 | 40.1132 | 14.281 | 198.8964 | 21.6936 | 39.9564 | 14.0018 | 196.3814 | 21.0512 | 35.0273 | 14.1032 | 196.4576 | 20.0021 | 42.1022 | 14.1369 | 198.096 | 194.8275 | 13.1896 | 53.2111 | 4.6567 | 9.982 | 0 | 75.3984 | 20.7757 | 58.2485 | 13.4066 | 191.1013 | 194.2313 | 12.9804 | 3.2783 | 61.3388 | 6.3512 | 67.69 | 15.1069 | 131.889 | 125.1203 | 99.9718 | 15.0861 | 17.879 | 191.9297 | 122.8993 | 14.8792 | 1.0464 | 38.7849 | 78.2126 | 1.5533 | 0.1112 | 0.078289 | 19.0173 | 0.65225 | 0.34021
2025-06-11 12:00 | 34.0262 | 5.887 | 0.94857 | 1.0011 | 20.9107 | 1.978 | 12.5703 | 192.5074 | 17.8627 | 191.8573 | 19.426 | 40.1122 | 14.2636 | 198.8236 | 21.6941 | 39.9567 | 13.9852 | 196.3209 | 20.8429 | 35.0265 | 14.0763 | 196.3816 | 20.003 | 42.1076 | 14.11 | 197.992 | 194.7702 | 13.1739 | 53.1282 | 4.786 | 9.9852 | 0 | 75.5113 | 20.7709 | 58.2409 | 13.3934 | 191.0703 | 194.1752 | 12.9647 | 3.2766 | 61.0034 | 6.301 | 67.3044 | 15.1004 | 131.7196 | 125.2239 | 99.9739 | 15.0803 | 17.8627 | 191.8573 | 123.1079 | 14.8626 | 1.0391 | 38.7395 | 78.4074 | 1.1472 | 0.11136 | 0.079215 | 18.8375 | 0.64227 | 0.33978
2025-06-11 13:00 | 33.8927 | 6.5113 | 0.94981 | 1.0018 | 21.1495 | 1.9582 | 12.5765 | 192.5256 | 17.8648 | 191.8707 | 19.3659 | 40.1111 | 14.2658 | 198.8335 | 21.7643 | 40.3568 | 14.0004 | 196.4025 | 20.7547 | 35.0275 | 14.0759 | 196.3886 | 20.0034 | 42.1068 | 14.119 | 198.0008 | 194.7719 | 12.5993 | 52.9842 | 4.9443 | 9.9843 | 0 | 75.5815 | 20.7613 | 58.2424 | 13.3941 | 191.0931 | 194.192 | 12.9709 | 3.1917 | 59.8996 | 6.4674 | 66.367 | 15.1045 | 131.5393 | 125.4067 | 99.9746 | 15.0848 | 17.8648 | 191.8707 | 123.2328 | 14.8645 | 1.0533 | 38.6856 | 78.4697 | 2.1148 | 0.11086 | 0.078794 | 18.5856 | 0.65383 | 0.33845
2025-06-11 14:00 | 34.2113 | 6.6931 | 0.94901 | 1.0029 | 21.1013 | 1.9109 | 12.5825 | 192.556 | 17.8916 | 191.7306 | 19.3541 | 40.1114 | 14.2989 | 198.943 | 16.6215 | 40.8682 | 14.055 | 196.6086 | 20.9963 | 35.0268 | 14.1311 | 196.5425 | 19.9925 | 42.1066 | 14.1568 | 198.1239 | 194.8393 | 6.167 | 53.5339 | 5.0595 | 9.9835 | 0 | 75.6422 | 20.7643 | 58.2327 | 13.4024 | 191.146 | 194.2309 | 12.9799 | 3.182 | 59.8836 | 5.4897 | 65.3733 | 15.1313 | 131.7255 | 125.49 | 99.9748 | 15.112 | 17.8916 | 191.7306 | 123.1278 | 14.8913 | 1.0869 | 38.6691 | 78.3795 | 2.8215 | 0.11014 | 0.078802 | 19.702 | 0.66745 | 0.33655
2025-06-11 15:00 | 34.5263 | 5.8321 | 0.9425 | 0.99516 | 20.6202 | 1.9 | 12.5952 | 192.5907 | 17.9207 | 191.5219 | 19.3706 | 40.1104 | 14.3371 | 199.0404 | 12.8896 | 40.9758 | 14.0918 | 196.754 | 21.1579 | 35.0248 | 14.1845 | 196.6751 | 20.0028 | 42.1014 | 14.1906 | 198.2313 | 194.914 | 5.0841 | 53.959 | 5.1551 | 9.9777 | 0 | 75.6984 | 20.766 | 58.2282 | 13.4168 | 191.1766 | 194.2715 | 12.9937 | 3.2513 | 60.7093 | 4.8922 | 65.6015 | 15.1508 | 131.9303 | 125.3641 | 99.9734 | 15.1318 | 17.9207 | 191.5219 | 123.2035 | 14.92 | 1.1226 | 38.7666 | 78.2206 | 2.6888 | 0.10979 | 0.077717 | 20.2805 | 0.67547 | 0.33566
2025-06-11 16:00 | 34.6778 | 4.5361 | 0.92705 | 0.97084 | 19.7066 | 1.9373 | 12.6442 | 192.744 | 17.9669 | 191.5291 | 19.3468 | 40.1102 | 14.3715 | 199.1711 | 18.3938 | 40.9706 | 14.1425 | 196.9304 | 20.9801 | 35.025 | 14.2337 | 196.7676 | 20.0295 | 42.0781 | 14.2374 | 198.3837 | 195.0586 | 11.579 | 53.9362 | 5.2913 | 9.9722 | 0 | 75.6596 | 20.7518 | 57.7644 | 13.4496 | 191.2192 | 194.4174 | 13.041 | 3.3919 | 61.9728 | 5.2069 | 67.1797 | 15.1799 | 132.0365 | 125.3195 | 99.9686 | 15.1597 | 17.9669 | 191.5291 | 123.007 | 14.9658 | 1.1511 | 38.8996 | 77.7027 | 2.8087 | 0.11127 | 0.073969 | 20.0604 | 0.71711 | 0.33632
2025-06-11 17:00 | 34.8725 | 6.0584 | 0.9101 | 0.94405 | 18.6824 | 1.8944 | 12.6657 | 192.8404 | 17.9942 | 191.5532 | 19.2884 | 40.1116 | 14.3661 | 199.2671 | 22.4402 | 40.9678 | 14.1763 | 197.0744 | 20.7942 | 35.0283 | 14.2518 | 196.8261 | 20.0057 | 42.0681 | 14.2619 | 198.5005 | 195.1697 | 13.2805 | 54.098 | 5.3772 | 9.971 | 0 | 75.5333 | 20.7483 | 56.737 | 13.4549 | 191.2767 | 194.5065 | 13.0621 | 3.4255 | 61.2767 | 4.7873 | 66.064 | 15.1986 | 132.1075 | 125.2524 | 99.9624 | 15.1757 | 17.9942 | 191.5532 | 122.7789 | 14.9938 | 1.1695 | 38.9911 | 77.0351 | 2.3915 | 0.12534 | 0.07118 | 20.4354 | 0.7688 | 0.33925
2025-06-11 18:00 | 35.0203 | 7.9611 | 0.89855 | 0.92834 | 18.1216 | 1.8274 | 12.7234 | 193.0552 | 18.049 | 191.4853 | 19.2984 | 39.7494 | 14.4 | 199.4653 | 23.0754 | 40.9677 | 14.2427 | 197.3471 | 20.9628 | 34.9699 | 14.3093 | 197.0839 | 20.0287 | 41.5626 | 14.3145 | 198.6533 | 195.4018 | 13.3447 | 54.3604 | 5.3566 | 9.9719 | 0 | 75.3946 | 20.8302 | 52.2168 | 13.4735 | 191.3771 | 194.6832 | 13.1115 | 3.267 | 59.079 | 4.9185 | 63.9975 | 15.2404 | 132.4119 | 125.0726 | 99.9587 | 15.2154 | 18.049 | 191.4853 | 122.754 | 15.049 | 1.1812 | 39.1939 | 76.4222 | 1.7435 | 0.14464 | 0.069852 | 19.8685 | 0.92119 | 0.34258
2025-06-11 19:00 | 35.1394 | 7.5499 | 0.89522 | 0.9238 | 17.9188 | 1.8815 | 12.731 | 193.0773 | 18.0499 | 191.6298 | 19.4225 | 38.7562 | 14.3854 | 199.4384 | 23.7758 | 40.9679 | 14.2547 | 197.4161 | 21.0819 | 34.9489 | 14.2984 | 197.056 | 19.9927 | 40.7253 | 14.2983 | 198.5878 | 195.4123 | 13.351 | 54.3788 | 5.3244 | 9.9741 | 0 | 75.2734 | 20.9703 | 51.9297 | 13.4888 | 191.3652 | 194.7016 | 13.1206 | 3.247 | 60.8161 | 5.299 | 66.1151 | 15.2373 | 132.4468 | 124.9123 | 99.9575 | 15.2113 | 18.0499 | 191.6298 | 122.1953 | 15.0497 | 1.1866 | 39.2159 | 75.7547 | 0.7835 | 0.15367 | 0.069411 | 20.2058 | 0.94151 | 0.3414
2025-06-11 20:00 | 34.9962 | 7.4628 | 0.89202 | 0.91813 | 17.7537 | 1.9483 | 12.6912 | 192.9538 | 17.9862 | 191.8104 | 19.5161 | 38.1249 | 14.3181 | 199.2388 | 23.8333 | 40.9684 | 14.1903 | 197.2553 | 20.8955 | 34.9494 | 14.2223 | 196.8054 | 20.0016 | 39.8884 | 14.22 | 198.3312 | 195.2501 | 13.2995 | 53.862 | 5.3313 | 9.9747 | 0 | 75.1612 | 21.0571 | 53.2157 | 13.4748 | 191.3218 | 194.589 | 13.0842 | 3.2321 | 62.411 | 5.7719 | 68.1829 | 15.1766 | 132.2772 | 124.637 | 99.9564 | 15.1506 | 17.9862 | 191.8104 | 121.924 | 14.986 | 1.1898 | 39.174 | 75.3864 | 0.10633 | 0.15725 | 0.069332 | 19.3447 | 0.90137 | 0.33991
2025-06-11 21:00 | 34.1614 | 6.5613 | 0.86815 | 0.89282 | 17.4629 | 2.0252 | 12.6509 | 192.8169 | 17.894 | 192.0822 | 19.8115 | 37.7606 | 14.2658 | 198.9852 | 23.8931 | 41.3537 | 14.1482 | 197.1657 | 20.919 | 35.6225 | 14.1871 | 196.7515 | 20.236 | 39.9433 | 14.1798 | 198.1148 | 194.9824 | 13.2206 | 51.9184 | 5.3946 | 9.9686 | 0 | 75.0491 | 21.053 | 54.1144 | 13.4537 | 191.299 | 194.4655 | 13.0435 | 3.4426 | 60.9983 | 8.1866 | 69.1849 | 15.0942 | 131.9509 | 124.3412 | 99.9555 | 15.0683 | 17.894 | 192.0822 | 122.4686 | 14.8938 | 1.1944 | 39.054 | 76.0367 | 10.2261 | 0.15969 | 0.069208 | 16.4153 | 0.91177 | 0.33979
2025-06-11 22:00 | 34.339 | 5.7668 | 0.8687 | 0.89319 | 17.2861 | 2.014 | 12.7089 | 193.0046 | 17.9749 | 191.8677 | 20.6465 | 38.7021 | 14.4413 | 199.4566 | 24.1416 | 41.4442 | 14.3079 | 197.6664 | 21.7379 | 35.8008 | 14.3497 | 197.3025 | 20.694 | 39.6256 | 14.3303 | 198.5859 | 195.188 | 13.2911 | 52.3167 | 5.4273 | 9.9626 | 0 | 74.9479 | 20.9421 | 52.4419 | 13.488 | 191.368 | 194.6522 | 13.1001 | 3.4998 | 61.2824 | 7.8767 | 69.1591 | 15.1649 | 132.209 | 124.6949 | 99.9558 | 15.1389 | 17.9749 | 191.8677 | 122.1634 | 14.9747 | 1.1984 | 39.144 | 75.6089 | 18.0562 | 0.16026 | 0.069067 | 16.4412 | 1.0001 | 0.34006
2025-06-11 23:00 | 34.9189 | 6.0673 | 0.8768 | 0.90049 | 16.9094 | 1.9141 | 12.6932 | 192.9525 | 18.0064 | 191.7743 | 21.4936 | 40.0304 | 14.5402 | 199.8135 | 23.8551 | 41.0669 | 14.3651 | 197.843 | 21.3478 | 35.1319 | 14.3694 | 197.3081 | 20.3995 | 40.1933 | 14.3675 | 198.7645 | 195.2413 | 13.3094 | 53.8704 | 5.404 | 9.9676 | 0 | 74.8598 | 20.9178 | 51.5902 | 13.4595 | 191.2309 | 194.5871 | 13.0834 | 3.2514 | 61.0806 | 5.7582 | 66.8388 | 15.1897 | 132.4507 | 124.7309 | 99.9562 | 15.1634 | 18.0064 | 191.7743 | 122.0833 | 15.0066 | 1.1997 | 39.2904 | 75.3 | 14.8704 | 0.16381 | 0.068926 | 19.3446 | 0.99081 | 0.34001
2025-06-12 | 35.7917 | 6.6006 | 0.88354 | 0.91724 | 16.2402 | 1.8659 | 12.9156 | 193.5329 | 18.2897 | 191.3921 | 21.9714 | 40.0526 | 14.8156 | 200.5704 | 25.8897 | 40.9854 | 14.6939 | 198.6458 | 20.1396 | 34.996 | 14.5996 | 197.6274 | 20.2552 | 42.0214 | 14.6548 | 199.4831 | 195.9087 | 13.5651 | 54.8455 | 5.4375 | 9.9728 | 0 | 74.7552 | 21.1 | 56.7765 | 13.7596 | 191.7543 | 195.2467 | 13.3342 | 3.4063 | 64.386 | 2.3991 | 66.7851 | 15.4145 | 133.7538 | 125.9917 | 99.9561 | 15.3872 | 18.2897 | 191.3921 | 122.4395 | 15.291 | 1.2021 | 39.975 | 76.0841 | 11.1244 | 0.16506 | 0.068832 | 20.6282 | 0.83235 | 0.33869
Total | MW: 830.9346; MVAR: 151.9453; kg/s: 4615217.171; kg/s: 282957.6797; kg/s: 5242529.0205; kg/s: 508670.4838; kg/s: 5751199.5043; kg/s: 11415254.1084
Average | 34.6223 | 6.3311 | 0.90233 | 0.94105 | 18.6949 | 1.9231 | 12.6457 | 192.7723 | 17.9486 | 191.7568 | 20.0644 | 39.7756 | 14.3608 | 199.2488 | 21.5431 | 40.4757 | 14.123 | 196.9009 | 20.6958 | 35.5934 | 14.2093 | 196.7817 | 20.0677 | 41.5992 | 14.23 | 198.362 | 195.0487 | 12.5239 | 53.4169 | 4.7677 | 9.974 | 0 | 75.237 | 20.8545 | 56.2872 | 13.4428 | 191.2048 | 194.4365 | 13.0425 | 3.275 | 60.6774 | 5.8874 | 66.5648 | 15.1504 | 132.121 | 124.8941 | 99.9627 | 15.1265 | 17.9486 | 191.7568 | 122.4372 | 14.9485 | 1.1548 | 39.0255 | 76.5645 | 4.6628 | 0.13524 | 0.072528 | 18.9737 | 0.80107 | 0.34229
Min | 33.8927 | 4.5361 | 0.86815 | 0.89282 | 16.2402 | 1.8274 | 12.5703 | 192.5074 | 17.8627 | 191.3921 | 19.2884 | 37.7606 | 14.2266 | 198.8236 | 12.8896 | 39.9515 | 13.9606 | 196.3209 | 19.7882 | 34.9489 | 14.0612 | 196.3291 | 19.9262 | 39.6256 | 14.11 | 197.992 | 194.7702 | 5.0841 | 51.9184 | 3.95 | 9.9626 | 0 | 74.7552 | 20.7365 | 51.5902 | 13.3687 | 191.004 | 194.1752 | 12.9647 | 3.1791 | 58.9466 | 2.3991 | 63.9975 | 15.0654 | 131.5393 | 124.108 | 99.9555 | 15.0392 | 17.8627 | 191.3921 | 121.6759 | 14.8626 | 1.0391 | 38.6691 | 75.3 | 0.10633 | 0.10979 | 0.068832 | 16.4153 | 0.64227 | 0.33566
Max | 35.7917 | 7.9611 | 0.94981 | 1.0029 | 21.1495 | 2.0252 | 12.9156 | 193.5329 | 18.2897 | 192.0822 | 22.2284 | 40.1132 | 14.8156 | 200.5704 | 25.8897 | 41.4442 | 14.6939 | 198.6458 | 21.7379 | 39.4539 | 14.5996 | 197.6274 | 20.694 | 42.1076 | 14.6548 | 199.4831 | 195.9087 | 13.5651 | 54.8455 | 5.4375 | 9.9852 | 0 | 75.6984 | 21.1 | 58.2548 | 13.7596 | 191.7543 | 195.2467 | 13.3342 | 3.4998 | 64.386 | 8.1866 | 69.1849 | 15.4145 | 133.7538 | 125.9917 | 99.9748 | 15.3872 | 18.2897 | 192.0822 | 123.2328 | 15.291 | 1.214 | 39.975 | 78.4697 | 18.0562 | 0.16506 | 0.079215 | 20.6282 | 1.0001 | 0.357

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1
18 |  | Night | 22:15 | 5.55 | 22.2
19 | 2025-06-10 | Day | 8:55 | 5.69 | 31.6
20 |  | Night | 0:20 | 5.18 | 24.3
21 | 2025-06-11 | Day | 17:00 | 5.07 | 21.6
22 |  | Night | 22:30 | 5.62 | 28.8
23 | 2025-06-12 | Day
24 |  | Night
25 | 2025-06-13 | Day
26 |  | Night
27 | 2025-06-14 | Day
28 |  | Night
29 | 2025-06-15 | Day
30 |  | Night
31 | 2025-06-16 | Day
32 |  | Night
33 | 2025-06-17 | Day
34 |  | Night
35 | 2025-06-18 | Day
36 |  | Night
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-11
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0