## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-12
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 21.1858 | 199.4157 | 37.6364
|  | #6-2 | Production | 21.7543 | 196.9652 | 37.254
|  | #6-3 | Production | 21.0919 | 196.9993 | 35.3827
|  | #6-4 | Production | 20.2519 | 198.3349 | 40.15
|  | #8-1 | Shut in | 5.9621 | 74.9822 | 9.9728
|  | #8-2 | Production | 20.8151 | 191.641 | 54.5027
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 51.9847 | 4491474.6614
|  | PAD #8 - STEAM |  |  |  |  | 3.6586 | 316101.0636 | Online
|  | BRINE HEADER |  |  |  |  | 23.4433 | 2025504.3798 | Offline
|  | TOTAL FLOW |  |  |  |  | 79.0866 | 6833080.1049
|  | PRESS SEPARATOR IJN 6 | Online | 13.3753 | 195.3878
|  | PRESS SEPARATOR IJN 8 | Online | 13.167 | 194.8398
| INJECTION WELL | #5-1 | Injection | 13.5043 | 116.9766 | 91.1391 | 129.8937 | 11222815.3448
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.8567 |  |  | 836.5601
|  | NET | 32.1232 |  |  | 770.9576
| PARASITIC LOAD |  | 2.7334 |  |  | 65.6025
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 2.2689 |  |  | 8168.0681
|  | NET | 2.462 |  |  | 8863.1075
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-12
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 770957.6055 |  | 0 |  | 770957.6055
|  |  |  | 770957.6055 |  | 0 |  | 770957.6055
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 771610 | [7 empty] | 771610
M-T-D GROSS GENERATION (kWHR) |  |  |  | 9938533 | [7 empty] | 9938533
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18436.28 | 0 | 4492.02 | 42.3 | 1192 | 1640 | 25802.6
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 219709.66 | -283254.3 | 69547.15 | 520 | 15939 | 18983 | 104989.15
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.8567 |  |  | 6.5868 |  | 18.5148
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 288
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 93.12%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 4491.4747 |  | 316.1011 |  |  | 5170.0874
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.051985 |  | 0.0036586 |  |  | 0.059839
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 2025.5044
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.023443
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 7195.5917
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.083282
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 193.2235 |  |  |  | 190.9379
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.7794 |  |  |  | 17.2695
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 15.3052 |  | 21.2472 |  |  | 18.5148
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [14 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [13 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:01 | PLN adviced load ROH 32.00 MW (Mr. Mochammad Bahrul Allam)
0:24 | Stop electrical pit pump IJN-6 (Level pond : 39.0%)
0:25 | Start pit pump IJN 8 (Level pond : 44.5%)
3:40 | Stop pit pump IJN 8 (Level pond : 38.1%)
3:41 | Start electrical pit pump IJN-6 (Level pond : 48.3%)
6:00 | Inspection of ACU & Air Purifier [standard activities schedule]
6:40 | Stop electrical pit pump IJN-6 (Level pond : 47.5%)
6:41 | Start pit pump IJN 8 (Level pond : 41.9%)
9:15 | Start air dryer-B due to prepare changeover air dryer (Dew point : -6 degC)
9:30 | Changeover air dryer-A to B
9:45 | Turn to standby mode for compressor-A
10:09 | Update pH brine+condensate inlet preheater (pH : 5.08 , Temp : 27.3 degC)
10:23 | Close manual valve before strainer reinjection pump-A due to prepare online cleaning preheater
10:43 | Stop pit pump IJN 8 (Level pond : 34.7%)
10:50 | Start electrical pit pump IJN-6 (Level pond : 56.8%)
13:37 | Top up seal oil tank from 79.9% into 91.2% (14 liter)
14:01 | PLN adviced load ROH 31.72 MW (Mr. Triashi Al Mutaqobili)
14:02 | Stop electrical pit pump IJN-6 (Level pomd : 46.5%)
14:10 | Start pit pump IJN-8 (Level pond : 39.7%)
16:54 | Install scalling coupon before online cleaning preheater at IJN 5 by Solenis
17:11 | Check level service water : 40.2%
17:14 | Start inject water from service water due to flushing injection line
17:28 | Turn to manual mode for brine bypass pre-heater-A&B due to make constant brine flow to preheater | [14 empty] | +
17:36 | Start Online cleaning preheater --> Injection Pressure : 17.7 Bar and Injection Flow : 70-140 liter/menit --> Delta Pressure : 3 Bar and Bypass Preheater Opening : 38-41%
17:48 | Adjust injection --> Pressure : 17.9 Bar and Injection Flow : 96 liter/menit
17:55 | Check pH outlet preheater (pH : 6.14) due to monitoring online cleaning preheater
17:59 | Adjust injection --> Pressure : 18 Bar, Injection flow : 90 liter/menit
18:02 | Check pH outlet preheater (pH : 7.13) due to monitoring online cleaning preheater
18:12 | Adjust injection --> Pressure : 18.1 Bar, Injection flow : 120 liter/menit
18:18 | Adjust injection--> Pressure : 18.2 Bar, Injection flow : 143 liter/menit
18:19 | Check pH outlet preheater (pH : 11.2) due to monitoring online cleaning preheater -=-> Delta Pressure Prehater : 2.5 Bar and Bypass Preheater Opening : 23%
18:30 | Adjust injection--> Pressure : 18 Bar, Injection flow : 148 liter/menit --> Delta Pressure Preheater : 2.4 Bar and Bypass Preheater Opening : 19%
18:32 | Adjust injection--> Pressure : 18.1 Bar, Injection flow : 152 liter/menit --> Delta Pressure Preheater : 2.35 Bar and Bypass Preheater Opening : 18%
18:39 | Adjust injection--> Pressure : 18.6 Bar, Injection flow : 148 liter/menit
18:46 | Check pH outlet preheater (pH : 11.76) due to monitoring online cleaning preheater
18:49 | Adjust injection--> Pressure : 17 Bar, Injection flow : 161 liter/menit --> Delta Pressure Preheater : 0.3 Bar and Bypass Preheater Opening :10%
18:50 | Turn to auto mode for brine bypass preheater-A&B due to delta pressure preheater already <3 Bar
18:54 | Adjust injection--> Pressure : 16.4 Bar, Injection flow : 151 liter/menit --> pH outlet preheater : 11.76
18:55 | Check pH outlet preheater (pH : 12.08) due to monitoring online cleaning preheater
19:05 | Adjust injection--> Pressure : 14.7 Bar, Injection flow : 110 liter/menit
19:22 | Stop Injection for online cleaning preheater --> Delta Pressure Preheater : 0.2 - 0.3 Bar
19:39 | Stop Injection pump after finish flushing the line
19:41 | Cleaning hose connection injection by Solenis
19:54 | Check level service water after online cleaning preheater already done --> Level before : 40.2 % , Level after : 39.9%
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Arbima |  |  |  | CCR Operator : Dwiki |  |  |  | Steamfield : Vandy
Night Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Tio |  |  |  | Steamfield : Rafly
22
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-12
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2188250 | 2188800 | 550 | 60950
(BACKUP) |  | 2126290 | 2186620 | 2187160 | 540 | 60870
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 101467150 | 102238760 | 771610 | 9136850
(BACKUP) |  | 93082960 | 101445830 | 102217210 | 771380 | 9134250
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4512310 | 4555020 | 42710 | 412790
(BACKUP) |  | 4144060 | 4514260 | 4556980 | 42720 | 412920
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 110423716 | 111261788 | 838072 | 9938533
TOTAL |  |  |  |  | 838072 | 9938533
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 18082581 | 18241841 | 159260 | 1711586
TOTAL |  |  |  |  | 159260 | 1711586
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3290591.72 | 3309028 | 18436.28 | 219709.66
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1054813.54 | 1059305.56 | 4492.02 | 69547.15
U Ijen 5 |  | 7258.6 | 7736.3 | 7778.6 | 42.3 | 520
U Ijen 6 |  | 247889 | 262636 | 263828 | 1192 | 15939
U Ijen 8 |  | 299837 | 317180 | 318820 | 1640 | 18983
TOTAL |  |  |  |  | 25802.6 | 324698.81
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-12 01:00 | 34.9957 | 5.5172 | 0.86573 | 0.90066 | 16.8433 | 1.9431 | 12.783 | 193.2391 | 18.0866 | 191.7743 | 22.0477 | 40.0367 | 14.6454 | 200.1416 | 24.108 | 40.9054 | 14.4348 | 197.9628 | 20.7037 | 34.8151 | 14.4352 | 197.4137 | 20.3074 | 40.7981 | 14.4514 | 198.8934 | 195.5223 | 13.4029 | 53.6471 | 5.5321 | 9.9688 | 0 | 74.6544 | 21.1437 | 49.2622 | 13.5407 | 191.4569 | 194.8551 | 13.1696 | 3.3087 | 62.087 | 5.9126 | 67.9996 | 15.2661 | 132.6242 | 125.0839 | 99.9565 | 15.2397 | 18.0866 | 191.7743 | 122.2265 | 15.0865 | 1.1999 | 39.3324 | 75.4805 | 13.5504 | 0.16359 | 0.068831 | 19.0423 | 1.1138 | 0.34129
2025-06-12 02:00 | 35.1258 | 6.4295 | 0.86603 | 0.89639 | 17.065 | 1.936 | 12.7101 | 193.0169 | 18.0261 | 191.6892 | 22.1478 | 39.5313 | 14.5849 | 199.9769 | 23.0953 | 39.913 | 14.3466 | 197.6771 | 21.431 | 34.9706 | 14.3924 | 197.3668 | 20.3067 | 41.2044 | 14.3943 | 198.7309 | 195.3163 | 13.3339 | 53.8849 | 5.5709 | 9.9653 | 0 | 74.5687 | 21.1969 | 51.1052 | 13.4954 | 191.383 | 194.6658 | 13.1045 | 3.3838 | 62.7098 | 5.2926 | 68.0024 | 15.2137 | 132.3653 | 124.6539 | 99.9564 | 15.1875 | 18.0261 | 191.6892 | 121.9327 | 15.026 | 1.1934 | 39.2501 | 75.0662 | 14.2741 | 0.16258 | 0.068868 | 19.9344 | 1.1109 | 0.34127
2025-06-12 03:00 | 35.314 | 7.3997 | 0.86453 | 0.88618 | 16.4876 | 1.9386 | 12.6669 | 192.8849 | 17.9931 | 191.2707 | 22.2056 | 39.0442 | 14.5361 | 199.8471 | 22.6436 | 38.9996 | 14.2863 | 197.5023 | 21.5569 | 34.9169 | 14.3466 | 197.2459 | 20.3035 | 40.9086 | 14.3423 | 198.6243 | 195.2095 | 13.2981 | 54.1459 | 5.6293 | 9.9677 | 0 | 74.4733 | 21.1296 | 51.2653 | 13.4481 | 191.2779 | 194.5422 | 13.0638 | 3.3008 | 63.9061 | 4.5554 | 68.4614 | 15.1844 | 132.3349 | 124.2538 | 99.9561 | 15.158 | 17.9931 | 191.2707 | 121.8996 | 14.9928 | 1.1898 | 39.2204 | 74.8754 | 12.0437 | 0.16898 | 0.06876 | 19.6965 | 0.98753 | 0.33972
2025-06-12 04:00 | 35.2829 | 7.2659 | 0.85504 | 0.86943 | 15.6737 | 1.9657 | 12.6668 | 192.8618 | 17.9787 | 191.2504 | 22.2374 | 39.0475 | 14.5048 | 199.7423 | 22.683 | 38.7307 | 14.2482 | 197.3241 | 21.1007 | 34.5814 | 14.3036 | 197.052 | 20.1881 | 40.9616 | 14.3072 | 198.5008 | 195.1439 | 13.2864 | 53.5264 | 5.7475 | 9.9671 | 0 | 74.3679 | 21.0362 | 54.1666 | 13.4625 | 191.2795 | 194.5381 | 13.0688 | 3.386 | 63.8129 | 5.5436 | 69.3565 | 15.1691 | 132.3486 | 124.2273 | 99.9548 | 15.1425 | 17.9787 | 191.2504 | 121.5643 | 14.9787 | 1.1985 | 39.1915 | 74.5163 | 11.3306 | 0.17926 | 0.068575 | 18.9606 | 0.99668 | 0.3393
2025-06-12 05:00 | 34.9986 | 6.9504 | 0.83754 | 0.85058 | 15.3052 | 1.9785 | 12.6072 | 192.6561 | 17.9052 | 191.7588 | 22.2512 | 39.0519 | 14.4159 | 199.4815 | 22.3184 | 38.3233 | 14.1348 | 196.925 | 20.9783 | 34.1451 | 14.2114 | 196.7623 | 20.1738 | 41.3964 | 14.2297 | 198.2966 | 194.876 | 13.2075 | 52.6726 | 5.9214 | 9.9643 | 0 | 74.2626 | 20.8731 | 58.2499 | 13.4243 | 191.1615 | 194.361 | 13.0147 | 3.3252 | 62.9115 | 6.3345 | 69.246 | 15.1056 | 132.0587 | 124.1877 | 99.9529 | 15.0789 | 17.9052 | 191.7588 | 121.5973 | 14.9054 | 1.2063 | 39.0579 | 74.6711 | 12.7601 | 0.1845 | 0.068408 | 18.4076 | 0.84118 | 0.34027
2025-06-12 06:00 | 34.7984 | 6.8603 | 0.83408 | 0.85369 | 15.7394 | 1.9919 | 12.5501 | 192.4669 | 17.8459 | 191.8843 | 22.2066 | 39.2678 | 14.3554 | 199.32 | 21.8946 | 38.6483 | 14.0646 | 196.7168 | 21.2356 | 34.1524 | 14.1542 | 196.5857 | 20.2444 | 41.7132 | 14.1931 | 198.2872 | 194.6911 | 13.1501 | 52.5867 | 6.2446 | 9.9688 | 0 | 74.1812 | 20.6832 | 58.2546 | 13.3549 | 190.9793 | 194.1626 | 12.9544 | 3.3054 | 62.7417 | 6.5742 | 69.316 | 15.0581 | 131.8024 | 124.1967 | 99.9545 | 15.0317 | 17.8459 | 191.8843 | 121.5403 | 14.8461 | 1.1976 | 38.869 | 74.8498 | 13.5582 | 0.17815 | 0.068835 | 17.8631 | 0.83393 | 0.34702
2025-06-12 07:00 | 34.6654 | 6.7758 | 0.85443 | 0.88939 | 17.0561 | 1.9892 | 12.5793 | 192.5563 | 17.876 | 191.5563 | 22.3161 | 39.773 | 14.4249 | 199.5027 | 21.4984 | 39.5423 | 14.1294 | 196.899 | 21.7039 | 35.7698 | 14.2337 | 196.953 | 20.1878 | 41.8966 | 14.2793 | 198.5917 | 194.8163 | 13.1946 | 52.8688 | 6.5987 | 9.9729 | 0 | 74.1962 | 20.6533 | 56.1904 | 13.3761 | 191.0238 | 194.2311 | 12.9791 | 3.1842 | 62.518 | 6.437 | 68.9551 | 15.0711 | 132.2442 | 123.7934 | 99.9606 | 15.0458 | 17.876 | 191.5563 | 121.3369 | 14.8757 | 1.153 | 39.0722 | 74.6753 | 17.1702 | 0.14676 | 0.071114 | 17.9451 | 0.80318 | 0.35809
2025-06-12 08:00 | 35.1922 | 6.2564 | 0.89073 | 0.93995 | 18.3941 | 1.9109 | 12.6743 | 192.891 | 17.997 | 188.7846 | 22.1483 | 40.0678 | 14.5729 | 199.8843 | 21.1417 | 39.9793 | 14.2474 | 197.2352 | 21.7752 | 36.5252 | 14.3443 | 197.3941 | 19.9993 | 41.3302 | 14.3719 | 198.8306 | 195.2822 | 13.339 | 54.6541 | 6.818 | 9.9734 | 0 | 74.3262 | 20.8132 | 50.8714 | 13.4426 | 191.1982 | 194.5176 | 13.0644 | 3.1984 | 62.9701 | 4.2782 | 67.2483 | 15.1774 | 133.0906 | 124.0815 | 99.9669 | 15.154 | 17.997 | 188.7846 | 121.7017 | 14.9967 | 1.078 | 39.4668 | 74.6892 | 10.5845 | 0.11708 | 0.074387 | 19.6031 | 0.73791 | 0.35634
2025-06-12 09:00 | 35.5781 | 6.1671 | 0.91942 | 0.97284 | 19.1601 | 1.879 | 12.6083 | 192.6653 | 17.9527 | 187.7474 | 21.1573 | 40.0729 | 14.4648 | 199.5361 | 20.8757 | 39.9883 | 14.1416 | 196.9437 | 20.9478 | 35.8952 | 14.2166 | 196.9723 | 19.9126 | 41.5095 | 14.2439 | 198.1108 | 195.1204 | 13.2934 | 55.4989 | 6.8773 | 9.9734 | 0 | 74.4856 | 21.0392 | 52.9284 | 13.4206 | 191.1751 | 194.3385 | 13.0102 | 3.4081 | 63.9705 | 2.8817 | 66.8522 | 15.1585 | 132.79 | 124.3541 | 99.9718 | 15.1374 | 17.9527 | 187.7474 | 121.8121 | 14.9529 | 1.0253 | 39.178 | 75.2182 | 0.72905 | 0.11157 | 0.076317 | 21.098 | 0.68249 | 0.3477
2025-06-12 10:00 | 35.3629 | 6.6588 | 0.93416 | 0.99088 | 19.7458 | 1.8956 | 12.5157 | 192.3365 | 17.8717 | 189.5226 | 20.3464 | 40.0756 | 14.3228 | 199.0809 | 20.8141 | 39.9912 | 14.0339 | 196.5717 | 20.6053 | 35.9833 | 14.1056 | 196.6787 | 20.1158 | 42.1055 | 14.1424 | 197.5734 | 194.7648 | 13.1905 | 54.95 | 6.8105 | 9.9745 | 0 | 74.6166 | 20.9878 | 58.2419 | 13.387 | 191.1156 | 194.0848 | 12.9349 | 3.4413 | 63.9225 | 3.1128 | 67.0353 | 15.0902 | 132.4604 | 124.0982 | 99.9745 | 15.0699 | 17.8717 | 189.5226 | 122.0633 | 14.8717 | 1.0063 | 38.9743 | 76.2371 | 1.1044 | 0.1117 | 0.077178 | 21.2541 | 0.6518 | 0.34506
2025-06-12 11:00 | 35.2629 | 6.2864 | 0.94318 | 1.0058 | 20.1756 | 1.8915 | 12.5284 | 192.3731 | 17.8992 | 190.1919 | 20.0569 | 40.077 | 14.3458 | 199.087 | 20.5791 | 39.9944 | 14.0597 | 196.5533 | 21.3596 | 35.9821 | 14.156 | 196.8365 | 20.1263 | 42.1084 | 14.1756 | 197.9664 | 194.8266 | 13.2115 | 54.9822 | 6.4798 | 9.9792 | 0 | 74.7629 | 20.7577 | 58.2201 | 13.3883 | 191.1283 | 194.1016 | 12.9421 | 3.3771 | 63.4886 | 3.2118 | 66.7004 | 15.1207 | 132.582 | 124.4078 | 99.9768 | 15.1007 | 17.8992 | 190.1919 | 122.361 | 14.8987 | 0.99544 | 39.0527 | 76.9952 | 1.5548 | 0.11173 | 0.078675 | 21.65 | 0.62828 | 0.34301
2025-06-12 12:00 | 35.0832 | 5.7229 | 0.94817 | 1.016 | 20.6005 | 1.8936 | 12.5058 | 192.2844 | 17.8657 | 190.3571 | 19.8811 | 40.0779 | 14.3127 | 198.9559 | 20.4614 | 39.9947 | 14.0275 | 196.4377 | 21.4898 | 35.9821 | 14.121 | 196.7208 | 19.9781 | 42.1047 | 14.1446 | 198.0941 | 194.7339 | 13.1856 | 54.8379 | 6.0105 | 9.9837 | 0 | 74.9503 | 20.6801 | 58.2233 | 13.3622 | 191.1035 | 193.9983 | 12.9151 | 3.362 | 62.8983 | 3.5337 | 66.432 | 15.103 | 132.2968 | 124.5838 | 99.9786 | 15.0841 | 17.8657 | 190.3571 | 122.3121 | 14.8654 | 0.99191 | 38.8943 | 77.1261 | 0.72325 | 0.11241 | 0.080408 | 21.5335 | 0.61889 | 0.34207
2025-06-12 13:00 | 34.8266 | 6.3007 | 0.94753 | 1.0075 | 21.1883 | 1.929 | 12.4588 | 192.1294 | 17.7997 | 190.6319 | 19.7942 | 40.0837 | 14.2334 | 198.7188 | 20.447 | 39.9936 | 13.958 | 196.2455 | 20.8637 | 35.9819 | 14.0187 | 196.4269 | 19.9444 | 42.0971 | 14.0689 | 197.8628 | 194.5345 | 13.1218 | 54.5086 | 5.7727 | 9.9857 | 0 | 75.1582 | 20.6795 | 58.2334 | 13.3174 | 191.036 | 193.8382 | 12.8655 | 3.3136 | 62.9141 | 4.2669 | 67.181 | 15.0509 | 132.043 | 124.6589 | 99.9808 | 15.0321 | 17.7997 | 190.6319 | 122.338 | 14.7998 | 0.99684 | 38.6743 | 77.1702 | 0.29042 | 0.11337 | 0.081009 | 20.7624 | 0.61879 | 0.34082
2025-06-12 14:00 | 34.8522 | 6.3996 | 0.92649 | 0.96161 | 21.2472 | 1.9539 | 12.4044 | 191.9429 | 17.7419 | 191.0998 | 19.672 | 40.0885 | 14.1696 | 198.5128 | 20.321 | 39.9948 | 13.9002 | 196.0657 | 20.8698 | 35.9836 | 13.983 | 196.2619 | 19.9738 | 42.0936 | 14.0214 | 197.7305 | 194.3308 | 13.0598 | 54.2915 | 5.728 | 9.9878 | 0 | 75.3745 | 20.6754 | 58.2227 | 13.2676 | 190.9006 | 193.6542 | 12.8099 | 3.3423 | 63.1759 | 4.9229 | 68.0988 | 15.0035 | 132.0708 | 124.5122 | 99.9861 | 14.9851 | 17.7419 | 191.0998 | 121.9198 | 14.7423 | 1.0171 | 38.5732 | 76.9059 | 1.3082 | 0.11411 | 0.080688 | 20.6475 | 0.63449 | 0.33601
2025-06-12 15:00 | 35.1123 | 5.5811 | 0.89903 | 0.9192 | 20.8477 | 1.9646 | 12.4623 | 192.119 | 17.7886 | 191.1148 | 19.6274 | 40.0857 | 14.2303 | 198.6528 | 20.3878 | 39.9947 | 13.9586 | 196.2244 | 21.3918 | 35.9652 | 14.0819 | 196.4696 | 20.0531 | 41.6706 | 14.0803 | 197.9211 | 194.5028 | 13.1222 | 54.4259 | 5.7484 | 9.9849 | 0 | 75.624 | 20.6912 | 56.2503 | 13.3105 | 190.9861 | 193.8197 | 12.8635 | 3.2593 | 63.5339 | 5.4479 | 68.9818 | 15.0268 | 132.7142 | 124.1289 | 99.9869 | 15.0094 | 17.7886 | 191.1148 | 121.659 | 14.7886 | 1.0616 | 38.9458 | 76.1896 | 1.9371 | 0.11439 | 0.07906 | 20.033 | 0.67117 | 0.33344
2025-06-12 16:00 | 34.7658 | 4.6054 | 0.88889 | 0.91233 | 19.9546 | 1.9823 | 12.558 | 192.4472 | 17.7788 | 190.3376 | 19.6058 | 40.0952 | 14.2832 | 198.7912 | 20.4776 | 39.9889 | 14.0041 | 196.3631 | 21.2958 | 35.9921 | 14.1376 | 196.5853 | 19.8655 | 40.9032 | 14.0964 | 197.9413 | 194.7564 | 13.198 | 53.868 | 5.6047 | 9.979 | 0 | 75.8077 | 20.7452 | 53.9154 | 13.3705 | 191.1592 | 194.0883 | 12.9448 | 3.086 | 62.4645 | 6.4528 | 68.9174 | 15.0077 | 132.7848 | 124.0159 | 99.9805 | 14.991 | 17.7788 | 190.3376 | 121.8183 | 14.7783 | 1.1031 | 38.996 | 75.8919 | 0.91831 | 0.11308 | 0.075702 | 16.2137 | 0.71049 | 0.3317
2025-06-12 17:00 | 34.309 | 5.8302 | 0.89422 | 0.92774 | 19.123 | 1.9862 | 12.55 | 192.4401 | 17.7544 | 186.2908 | 19.4763 | 40.1051 | 14.2102 | 198.6815 | 20.2548 | 39.9816 | 13.9457 | 196.2014 | 20.8059 | 36.0324 | 14.0853 | 196.4145 | 19.8451 | 41.3112 | 14.052 | 197.6978 | 194.6732 | 13.1616 | 53.0431 | 5.3064 | 9.9747 | 0 | 75.7728 | 20.8012 | 55.0147 | 13.3605 | 191.187 | 194.0875 | 12.9403 | 3.1696 | 61.3666 | 6.7788 | 68.1454 | 14.9835 | 132.2114 | 124.0515 | 99.9717 | 14.9643 | 17.7544 | 186.2908 | 121.5336 | 14.7534 | 1.2036 | 38.2233 | 75.6958 | 1.2812 | 0.1185 | 0.072318 | 15.8248 | 0.74533 | 0.33485
2025-06-12 18:00 | 34.7976 | 7.7093 | 0.91343 | 0.95071 | 18.7914 | 2.4666 | 12.7186 | 193.0015 | 17.7125 | 183.9485 | 19.4752 | 39.4673 | 14.2961 | 199.1049 | 20.3034 | 39.3664 | 14.0684 | 196.592 | 20.992 | 35.5814 | 14.2157 | 196.8159 | 20.3559 | 40.6947 | 14.206 | 198.2461 | 195.1833 | 13.3156 | 52.5995 | 5.1961 | 9.9689 | 0 | 75.6272 | 20.779 | 53.3367 | 13.4978 | 191.5418 | 194.6445 | 13.108 | 3.432 | 59.6023 | 26.2292 | 85.8316 | 15.2116 | 134.7391 | 123.8675 | 99.9623 | 15.1853 | 17.7125 | 183.9485 | 113.5939 | 15.2639 | 1.3199 | 27.754 | 78.944 | 1.8499 | 0.1327 | 0.070414 | 15.2157 | 0.96909 | 0.34129
2025-06-12 19:00 | 35.1251 | 8.4453 | 0.92762 | 0.96072 | 18.6368 | 3.3941 | 12.9644 | 193.862 | 16.2666 | 189.0259 | 20.644 | 34.4842 | 14.3507 | 199.3275 | 21.2975 | 34.4771 | 14.157 | 196.9953 | 21.2153 | 37.0177 | 14.338 | 197.2299 | 20.2598 | 38.5976 | 14.2842 | 198.6027 | 195.8601 | 13.5089 | 50.1312 | 5.396 | 9.9667 | 0 | 75.5208 | 20.9128 | 46.0195 | 13.6601 | 191.9687 | 195.3506 | 13.315 | 3.4263 | 54.366 | 64.8514 | 119.2174 | 12.7331 | 132.6175 | 113.637 | 99.9573 | 12.7041 | 16.2666 | 189.0259 | 98.3916 | 14.7948 | 1.272 | 9.0814 | 87.6413 | 0.67948 | 0.14054 | 0.070067 | 6.1479 | 2.0985 | 0.34303
2025-06-12 20:00 | 34.7856 | 8.3294 | 0.92415 | 0.95197 | 18.6171 | 3.7461 | 13.2225 | 194.7454 | 14.9886 | 193.8665 | 22.6519 | 27.5928 | 14.3743 | 199.3864 | 22.9758 | 27.6035 | 14.2139 | 197.3581 | 21.3843 | 37.8308 | 14.4256 | 197.5231 | 20.0892 | 37.1635 | 14.3337 | 198.1994 | 196.4926 | 13.6954 | 46.6574 | 5.6698 | 9.9687 | 0 | 75.4435 | 21.083 | 52.0609 | 13.9677 | 192.875 | 196.2166 | 13.5723 | 3.7955 | 50.2649 | 80.0465 | 130.3115 | 9.2721 | 124.7201 | 97.8505 | 91.8428 | 9.1845 | 14.9886 | 193.8665 | 90.5685 | 13.6719 | 1.1136 | 0.79186 | 92.5587 | 0.10726 | 0.14154 | 0.070203 | 0.085619 | 3.2358 | 0.34283
2025-06-12 21:00 | 33.9691 | 7.1139 | 0.9034 | 0.92833 | 18.7324 | 3.653 | 13.2553 | 194.865 | 15.5586 | 194.1801 | 23.1175 | 27.3381 | 14.3445 | 199.2613 | 23.7245 | 26.4537 | 14.1668 | 197.2221 | 20.7446 | 35.9272 | 14.3412 | 197.098 | 20.4468 | 35.7454 | 14.2852 | 197.966 | 196.481 | 13.7011 | 45.1433 | 5.8059 | 9.9693 | 0 | 75.3815 | 20.7169 | 60.2998 | 14.0566 | 193.1139 | 196.3961 | 13.6304 | 3.8638 | 51.3509 | 72.7397 | 124.0906 | 9.2818 | 117.2358 | 91.8567 | 56.7853 | 7.6715 | 15.5586 | 194.1801 | 88.7104 | 14.1785 | 1.0318 | 1.4941 | 90.326 | 0.10731 | 0.142 | 0.070178 | 1.3637 | 2.7748 | 0.98194
2025-06-12 22:00 | 33.5121 | 6.7612 | 0.88101 | 0.90761 | 18.8062 | 3.8153 | 13.2513 | 194.893 | 15.6072 | 194.4139 | 22.3539 | 30.5935 | 14.3827 | 199.3758 | 23.529 | 28.9817 | 14.1703 | 197.1105 | 20.0269 | 34.3781 | 14.3052 | 196.8733 | 20.6909 | 35.2026 | 14.2837 | 198.2775 | 196.436 | 13.6895 | 44.99 | 5.997 | 9.9683 | 0 | 75.343 | 20.3225 | 58.2898 | 13.9998 | 192.9385 | 196.3525 | 13.6168 | 4.3878 | 51.7787 | 76.08 | 127.8587 | 9.1908 | 118.1515 | 90.4169 | 39.7947 | 7.5565 | 15.6072 | 194.4139 | 88.1862 | 14.5719 | 1.0267 | 1.2837 | 90.1831 | 0.10736 | 0.1403 | 0.070194 | 1.3645 | 2.1172 | 1.6407
2025-06-12 23:00 | 33.8859 | 6.6698 | 0.86786 | 0.89034 | 18.5178 | 3.8458 | 13.3375 | 195.1908 | 15.191 | 194.9767 | 21.7943 | 32.2885 | 14.4978 | 199.7408 | 23.5042 | 30.3575 | 14.2769 | 197.2996 | 20.6092 | 32.8206 | 14.3965 | 197.2596 | 21.0387 | 35.0705 | 14.3812 | 198.4348 | 196.7181 | 13.7759 | 45.1331 | 6.2221 | 9.9672 | 0 | 75.3222 | 20.4049 | 53.6443 | 14.0396 | 193.0646 | 196.5829 | 13.6857 | 6.1794 | 48.0978 | 82.222 | 130.3198 | 8.2901 | 123.296 | 90.1536 | 49.7646 | 8.0976 | 15.191 | 194.9767 | 89.0895 | 14.4736 | 1.0223 | 0.50126 | 91.6346 | 0.1076 | 0.13655 | 0.070349 | 0.085859 | 2.1659 | 1.6956
2025-06-13 | 34.9588 | 6.0456 | 0.79976 | 0.81805 | 17.6452 | 3.5532 | 14.1273 | 197.4958 | 14.9811 | 194.8347 | 21.2454 | 34.9273 | 15.2358 | 201.8669 | 22.7662 | 31.893 | 15.0129 | 198.7394 | 21.1183 | 31.9553 | 15.1052 | 199.0425 | 21.6388 | 35.0139 | 15.1065 | 200.6584 | 199.035 | 14.5629 | 44.5848 | 6.4017 | 9.9674 | 0 | 75.3525 | 20.7566 | 45.7977 | 14.718 | 194.3305 | 198.7266 | 14.4348 | 6.5692 | 49.2825 | 74.9338 | 124.2164 | 7.4559 | 115.8662 | 86.3674 | 49.7661 | 7.2924 | 14.9811 | 194.8347 | 86.2355 | 14.3272 | 1.0253 | 0.33686 | 91.7577 | 0.10751 | 0.13217 | 0.0702 | 0.085692 | 0.95628 | 0.48283
Total | MW: 836.5601; MVAR: 158.0822; kg/s: 4491474.6614; kg/s: 316101.0636; kg/s: 5170087.3679; kg/s: 2025504.3798; kg/s: 7195591.7477; kg/s: 11222815.3448
Average | 34.8567 | 6.5868 | 0.8911 | 0.92533 | 18.5148 | 2.396 | 12.7794 | 193.2235 | 17.2695 | 190.9379 | 21.1858 | 37.6364 | 14.4206 | 199.4157 | 21.7543 | 37.254 | 14.1661 | 196.9652 | 21.0919 | 35.3827 | 14.2689 | 196.9993 | 20.2519 | 40.15 | 14.2698 | 198.3349 | 195.3878 | 13.3753 | 51.9847 | 5.9621 | 9.9728 | 0 | 74.9822 | 20.8151 | 54.5027 | 13.5695 | 191.641 | 194.8398 | 13.167 | 3.6586 | 59.839 | 23.4433 | 83.2823 | 13.6761 | 129.8937 | 116.9766 | 91.1391 | 13.5043 | 17.2695 | 190.9379 | 113.5997 | 14.7684 | 1.1095 | 29.3423 | 79.5541 | 4.9244 | 0.13698 | 0.072947 | 14.7841 | 1.1543 | 0.48526
Min | 33.5121 | 4.6054 | 0.79976 | 0.81805 | 15.3052 | 1.879 | 12.4044 | 191.9429 | 14.9811 | 183.9485 | 19.4752 | 27.3381 | 14.1696 | 198.5128 | 20.2548 | 26.4537 | 13.9002 | 196.0657 | 20.0269 | 31.9553 | 13.983 | 196.2619 | 19.8451 | 35.0139 | 14.0214 | 197.5734 | 194.3308 | 13.0598 | 44.5848 | 5.1961 | 9.9643 | 0 | 74.1812 | 20.3225 | 45.7977 | 13.2676 | 190.9006 | 193.6542 | 12.8099 | 3.086 | 48.0978 | 2.8817 | 66.432 | 7.4559 | 115.8662 | 86.3674 | 39.7947 | 7.2924 | 14.9811 | 183.9485 | 86.2355 | 13.6719 | 0.99191 | 0.33686 | 74.5163 | 0.10726 | 0.11157 | 0.068408 | 0.085619 | 0.61879 | 0.3317
Max | 35.5781 | 8.4453 | 0.94817 | 1.016 | 21.2472 | 3.8458 | 14.1273 | 197.4958 | 18.0866 | 194.9767 | 23.1175 | 40.1051 | 15.2358 | 201.8669 | 24.108 | 40.9054 | 15.0129 | 198.7394 | 21.7752 | 37.8308 | 15.1052 | 199.0425 | 21.6388 | 42.1084 | 15.1065 | 200.6584 | 199.035 | 14.5629 | 55.4989 | 6.8773 | 9.9878 | 0 | 75.8077 | 21.1969 | 60.2998 | 14.718 | 194.3305 | 198.7266 | 14.4348 | 6.5692 | 63.9705 | 82.222 | 130.3198 | 15.2661 | 134.7391 | 125.0839 | 99.9869 | 15.2397 | 18.0866 | 194.9767 | 122.361 | 15.2639 | 1.3199 | 39.4668 | 92.5587 | 17.1702 | 0.1845 | 0.081009 | 21.65 | 3.2358 | 1.6956

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1
18 |  | Night | 22:15 | 5.55 | 22.2
19 | 2025-06-10 | Day | 8:55 | 5.69 | 31.6
20 |  | Night | 0:20 | 5.18 | 24.3
21 | 2025-06-11 | Day | 17:00 | 5.07 | 21.6
22 |  | Night | 22:30 | 5.62 | 28.8
23 | 2025-06-12 | Day | 10:10 | 5.08 | 27.3
24 |  | Night | 21:30 | 5.64 | 26.6
25 | 2025-06-13 | Day
26 |  | Night
27 | 2025-06-14 | Day
28 |  | Night
29 | 2025-06-15 | Day
30 |  | Night
31 | 2025-06-16 | Day
32 |  | Night
33 | 2025-06-17 | Day
34 |  | Night
35 | 2025-06-18 | Day
36 |  | Night
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-12
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0