## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-13
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 23.7213 | 198.9645 | 25.9791
|  | #6-2 | Production | 25.9376 | 196.8405 | 27.2405
|  | #6-3 | Production | 20.638 | 197.1809 | 37.2029
|  | #6-4 | Production | 21.4043 | 198.1294 | 36.2119
|  | #8-1 | Shut in | 5.9387 | 77.2814 | 9.9746
|  | #8-2 | Production | 22.956 | 192.3541 | 37.3608
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 44.4731 | 3842476.9283
|  | PAD #8 - STEAM |  |  |  |  | 3.7487 | 323884.8703 | Online
|  | BRINE HEADER |  |  |  |  | 88.327 | 7631450.4758 | Offline
|  | TOTAL FLOW |  |  |  |  | 136.5488 | 11797812.2744
|  | PRESS SEPARATOR IJN 6 | Online | 13.5602 | 196.0009
|  | PRESS SEPARATOR IJN 8 | Online | 13.4314 | 195.7523
| INJECTION WELL | #5-1 | Injection | 8.5976 | 91.4633 | 42.5782 | 133.4273 | 11528116.9087
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.5652 |  |  | 829.5654
|  | NET | 31.8628 |  |  | 764.707
| PARASITIC LOAD |  | 2.7024 |  |  | 64.8585
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 3.9505 |  |  | 14221.6776
|  | NET | 4.2855 |  |  | 15427.8863
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-13
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 764706.9765 |  | 0 |  | 764706.9765
|  |  |  | 764706.9765 |  | 0 |  | 764706.9765
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 764030 | [7 empty] | 764030
M-T-D GROSS GENERATION (kWHR) |  |  |  | 10767237 | [7 empty] | 10767237
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18321.47 | 0 | 3389.07 | 44 | 857 | 960 | 23571.54
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 238031.13 | -283254.3 | 72936.22 | 564 | 16796 | 19943 | 110239.22
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.5652 |  |  | 7.2306 |  | 18.8618
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 312
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 92.37%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 3842.4769 |  | 323.8849 |  |  | 4249.7823
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.044473 |  | 0.0037487 |  |  | 0.049187
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 7631.4505
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.088327
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 11881.2328
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.13751
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 194.3934 |  |  |  | 194.5952
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 13.1208 |  |  |  | 14.2781
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 17.2183 |  | 21.5247 |  |  | 18.8618
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [14 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [13 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:01 | PLN adviced load ROH 31.72 MW (Mr. Mochammad Bahrul Allam)
0:20 | Start electrical pit pump IJN-6 (Level pond : 42.6%)with pressure 17.8 bar and current 93 A
4:20 | Stop electrical pit pump IJN-6 (Level pond : 29.3%)
4:21 | Start pit pump IJN 8 (Level pond : 33.5%)
6:05 | Full open isolasi valve suction Reinjection pump A
7:00 | Changeover strainer inlet preheater from strainer B to strainer A due DP reach 0.68bar
7:31 | Stop pit pump IJN 8 (Level pond : 38.1%)
8:40 | Check pH brine+condensate inlet preheater (pH : 5.11 , Temperature : 27.1 degC)
9:15 | Seal oil auto started
9:52 | Online stroke test MOV IJN-5.1 (PV-2705A) --> Result : Good and normal
9:55 | Exercise master valve IJN 5-1 (around 10%) due to heavy to rotate (Standard Activity)
10:00 | Install door closer at electrical room
10:34 | Exercise master valve IJN 2-1 --> Result : Good and normal condition (Standard Activity)
13:28 | Start P8202 refilling Pump --> Level fire water tank : 74.86%
13:34 | Stop P8202 refilling pump
14:05 | Dismantle strainer-B brine gathering due to cleaning strainer
14:19 | Running test jockey pump --> Cut-in : 8.36 and Cut-out : 9.23 (Standard Activity)
14:31 | Running test electrical fire pump --> Cut-in : 6.7 Bar and cut-out : 13.6 Bar (Standard Activity)
14:48 | Running test diesel fire pump (Standard Activity)
16:30 | Change priority CV rock muffler (PV-2430B to 2430A)
18:30 | Switch Reinjection Booster pump B to A due to strainer dirty (value : 0.26)
21:33 | Draining of Air Vessel Tank on IJN 8 [standard activities schedule]
21:51 | Draining of Air Vessel Tank on IJN 6 [standard activities schedule]
22:20 | Draining of Air Vessel Tank on Power Block [standard activities schedule]
IX.) SERVICE REQUEST
SR-06-2025-0006 | Differential pressure of Strainer - SP-2501A & SP-2501B of brine gathering reach 0.68 [Need to cleaning strainer]
SR-06-2025-0007 | Differential pressure of strainer Reinjection Pump-B (ST-2601B) already 0.26 Bar and reach alarm [Need to cleaning strainer]
X.) SHIFT CREW
Day Shift | Shift Leader : Arbima |  |  |  | CCR Operator : Dwiki |  |  |  | Steamfield : Vandy
Night Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Tio |  |  |  | Steamfield : Rafly
22
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-13
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2188800 | 2189100 | 300 | 61250
(BACKUP) |  | 2126290 | 2187160 | 2187470 | 310 | 61180
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 102238760 | 103002790 | 764030 | 9900880
(BACKUP) |  | 93082960 | 102217210 | 102981030 | 763820 | 9898070
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4555020 | 4615050 | 60030 | 472820
(BACKUP) |  | 4144060 | 4556980 | 4617010 | 60030 | 472950
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 111261788 | 112090492 | 828704 | 10767237
TOTAL |  |  |  |  | 828704 | 10767237
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 18241841 | 18416276 | 174435 | 1886021
TOTAL |  |  |  |  | 174435 | 1886021
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3309028 | 3327349.47 | 18321.47 | 238031.13
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1059305.56 | 1062694.63 | 3389.07 | 72936.22
U Ijen 5 |  | 7258.6 | 7778.6 | 7822.6 | 44 | 564
U Ijen 6 |  | 247889 | 263828 | 264685 | 857 | 16796
U Ijen 8 |  | 299837 | 318820 | 319780 | 960 | 19943
TOTAL |  |  |  |  | 23571.54 | 348270.35
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-13 01:00 | 34.0846 | 6.6079 | 0.80064 | 0.80563 | 17.4886 | 3.6973 | 13.6054 | 196.0447 | 14.7568 | 195.9074 | 20.9253 | 33.5796 | 14.7472 | 200.5155 | 23.2992 | 30.2887 | 14.5198 | 198.2476 | 21.3055 | 33.2056 | 14.6508 | 198.2056 | 21.4292 | 34.1097 | 14.6217 | 199.3156 | 197.5474 | 14.0267 | 44.1526 | 6.6223 | 9.9676 | 0 | 75.424 | 21.3475 | 39.0628 | 14.2119 | 193.6345 | 197.3231 | 13.9162 | 2.4869 | 47.6231 | 78.3971 | 126.0201 | 7.9966 | 123.2319 | 90.8484 | 49.7663 | 7.8087 | 14.7568 | 195.9074 | 88.7843 | 13.86 | 1.0331 | 0.34168 | 92.1242 | 0.10767 | 0.13473 | 0.070329 | 0.08579 | 1.565 | 1.0919
2025-06-13 02:00 | 32.2228 | 6.887 | 0.79427 | 0.80441 | 17.4066 | 4.0363 | 13.3594 | 195.2736 | 14.504 | 195.2045 | 21.13 | 30.0775 | 14.3926 | 199.2881 | 23.8401 | 28.3733 | 14.2005 | 197.302 | 21.5572 | 33.0412 | 14.3502 | 197.3905 | 21.523 | 33.3287 | 14.3046 | 198.3797 | 196.579 | 13.7281 | 41.5848 | 6.8005 | 9.9714 | 0 | 75.4855 | 21.8233 | 38.7661 | 13.9678 | 192.909 | 196.5025 | 13.6563 | 4.1836 | 44.8962 | 85.1651 | 130.0613 | 8.5069 | 127.99 | 91.4509 | 49.7661 | 8.3012 | 14.504 | 195.2045 | 89.6024 | 13.6712 | 1.037 | 0.34229 | 92.367 | 0.10725 | 0.14308 | 0.069772 | 0.085261 | 3.019 | 2.5587
2025-06-13 03:00 | 32.0642 | 6.7569 | 0.79003 | 0.80301 | 17.606 | 4.3739 | 13.2546 | 194.9377 | 14.5082 | 195.0006 | 21.6108 | 26.6063 | 14.2128 | 198.6718 | 24.7942 | 26.3668 | 14.0524 | 196.8474 | 21.6412 | 33.7642 | 14.2381 | 197.1543 | 21.4308 | 34.3717 | 14.1789 | 198.049 | 196.1457 | 13.5912 | 39.4586 | 6.9517 | 9.9747 | 0 | 75.5285 | 21.7681 | 51.5296 | 13.9902 | 193.0198 | 196.3073 | 13.5857 | 6.4933 | 42.5109 | 97.7361 | 140.247 | 9.5319 | 134.3989 | 91.5945 | 49.7663 | 9.3044 | 14.5082 | 195.0006 | 90.4375 | 13.6828 | 1.037 | 0.34223 | 92.2606 | 0.85996 | 0.1478 | 0.069308 | 1.0013 | 3.0184 | 2.5612
2025-06-13 04:00 | 34.1144 | 6.6021 | 0.82951 | 0.842 | 17.7077 | 4.288 | 13.2786 | 194.9223 | 14.8531 | 195.1709 | 22.4101 | 26.1393 | 14.3421 | 199.1029 | 25.535 | 25.9888 | 14.1674 | 197.1083 | 21.9013 | 35.9587 | 14.415 | 197.8519 | 21.5276 | 36.3291 | 14.3235 | 198.1529 | 196.321 | 13.659 | 41.1148 | 7.1257 | 9.9736 | 0 | 75.5747 | 21.2203 | 52.2149 | 13.9945 | 193.0046 | 196.3637 | 13.6167 | 6.6617 | 41.9902 | 104.2919 | 146.2821 | 10.5718 | 139.4937 | 91.9299 | 49.7665 | 10.3284 | 14.8531 | 195.1709 | 90.8734 | 13.9866 | 1.0336 | 0.34093 | 92.4478 | 0.86059 | 0.1445 | 0.069224 | 1.1504 | 1.5995 | 1.124
2025-06-13 05:00 | 34.5718 | 6.6447 | 0.84211 | 0.85808 | 17.9464 | 4.1571 | 13.3705 | 195.2242 | 14.9018 | 195.2328 | 23.5386 | 26.1361 | 14.5208 | 199.6627 | 25.6938 | 25.9897 | 14.314 | 197.4807 | 21.8368 | 36.4247 | 14.5724 | 198.4193 | 21.7463 | 36.4047 | 14.4732 | 198.4406 | 196.7247 | 13.7837 | 43.1874 | 7.3153 | 9.9668 | 0 | 75.6438 | 21.473 | 37.9816 | 13.9307 | 192.751 | 196.5206 | 13.6634 | 4.4228 | 42.4541 | 101.2658 | 143.7199 | 10.7502 | 139.8061 | 92.3653 | 49.768 | 10.5062 | 14.9018 | 195.2328 | 90.7842 | 14.0539 | 1.0293 | 0.341 | 92.5992 | 0.10751 | 0.13757 | 0.069598 | 0.55651 | 1.5989 | 1.1207
2025-06-13 06:00 | 34.6874 | 6.7276 | 0.83831 | 0.85253 | 18.4448 | 4.1673 | 13.364 | 195.1652 | 14.6816 | 195.389 | 24.3054 | 26.1339 | 14.5396 | 199.7147 | 25.8716 | 26.3777 | 14.3097 | 197.4856 | 20.9292 | 36.8633 | 14.5327 | 198.1244 | 21.4793 | 36.0876 | 14.4601 | 198.5665 | 196.7281 | 13.7841 | 43.7557 | 7.5179 | 9.9679 | 0 | 75.7645 | 22.3478 | 35.4409 | 13.9353 | 192.7966 | 196.4849 | 13.6502 | 3.0852 | 45.1461 | 99.408 | 144.5541 | 10.3872 | 138.5598 | 92.1446 | 49.7698 | 10.146 | 14.6816 | 195.389 | 90.322 | 14.0427 | 1.0197 | 0.34698 | 92.4651 | 0.10826 | 0.12911 | 0.070679 | 0.40916 | 0.9166 | 0.44834
2025-06-13 07:00 | 34.6071 | 7.0555 | 0.87152 | 0.89013 | 18.8948 | 4.0797 | 13.1158 | 194.4157 | 14.2925 | 194.8619 | 24.7496 | 26.1344 | 14.3544 | 199.1479 | 25.9672 | 27.0808 | 14.1069 | 196.8846 | 20.8517 | 37.1824 | 14.3163 | 197.3749 | 21.3074 | 36.0271 | 14.251 | 197.9656 | 196.0288 | 13.5616 | 44.7978 | 7.6379 | 9.9753 | 0 | 75.9699 | 22.7382 | 35.6842 | 13.7355 | 192.3034 | 195.7799 | 13.4241 | 3.5449 | 48.4402 | 92.7462 | 141.1865 | 9.7646 | 135.9461 | 91.4308 | 49.7726 | 9.5333 | 14.2925 | 194.8619 | 90.1423 | 13.8702 | 0.99888 | 0.34735 | 91.9715 | 0.10987 | 0.11919 | 0.072258 | 0.088133 | 1.4868 | 1.0314
2025-06-13 08:00 | 34.8268 | 8.134 | 0.89249 | 0.91415 | 19.4475 | 3.8352 | 12.9768 | 193.9904 | 13.9117 | 194.4447 | 24.7926 | 26.133 | 14.2527 | 198.8653 | 25.9489 | 27.6897 | 13.9985 | 196.5707 | 20.8717 | 36.6458 | 14.1846 | 196.8762 | 21.4249 | 35.7487 | 14.1384 | 197.7793 | 195.6948 | 13.4514 | 46.2425 | 7.61 | 9.9763 | 0 | 76.1883 | 22.9369 | 34.8612 | 13.6138 | 191.9541 | 195.3675 | 13.2936 | 3.663 | 51.7612 | 81.8073 | 133.5685 | 8.8644 | 130.6077 | 91.3275 | 49.7765 | 8.6554 | 13.9117 | 194.4447 | 89.7008 | 13.5177 | 0.96975 | 0.33909 | 91.196 | 0.11149 | 0.11209 | 0.073672 | 0.089311 | 1.4265 | 0.97866
2025-06-13 09:00 | 34.9914 | 9.1492 | 0.89361 | 0.91619 | 20.4783 | 3.7393 | 13.0356 | 194.0925 | 13.7907 | 194.4032 | 24.5483 | 26.1351 | 14.3082 | 199.0155 | 26.0977 | 27.9983 | 14.0653 | 196.7445 | 20.6043 | 36.9458 | 14.2355 | 196.9416 | 21.4856 | 35.6344 | 14.2059 | 198.0825 | 195.8622 | 13.5219 | 46.6356 | 7.4532 | 9.9792 | 0 | 76.4904 | 23.1262 | 34.841 | 13.6795 | 192.1437 | 195.4911 | 13.3479 | 3.5108 | 54.1868 | 76.6565 | 130.8433 | 8.3213 | 128.5788 | 91.4507 | 48.8659 | 8.1044 | 13.7907 | 194.4032 | 89.3839 | 13.378 | 0.91928 | 0.30465 | 91.5602 | 0.11469 | 0.11284 | 0.076583 | 0.092169 | 0.7971 | 0.38818
2025-06-13 10:00 | 34.9933 | 9.0254 | 0.91859 | 0.94389 | 21.5247 | 3.7915 | 13.0473 | 194.0831 | 13.9689 | 194.3375 | 24.2946 | 26.1479 | 14.3509 | 199.0416 | 26.2068 | 28.0175 | 14.1103 | 196.8293 | 20.8423 | 37.6702 | 14.3049 | 197.1356 | 21.5136 | 35.6709 | 14.2489 | 198.1403 | 195.879 | 13.5436 | 46.9214 | 7.1307 | 9.9858 | 0 | 76.9554 | 23.2583 | 34.9252 | 13.7086 | 192.2574 | 195.4828 | 13.3595 | 3.6403 | 53.2879 | 79.3905 | 132.6785 | 8.4364 | 130.1253 | 91.3856 | 43.6303 | 8.101 | 13.9689 | 194.3375 | 89.646 | 13.5402 | 0.87133 | 0.25579 | 92.0756 | 0.11861 | 0.117 | 0.0798 | 0.095415 | 0.72999 | 0.38149
2025-06-13 11:00 | 34.9203 | 6.6983 | 0.91815 | 0.93856 | 21.2819 | 3.7513 | 12.995 | 193.9878 | 13.9376 | 194.242 | 24.162 | 26.139 | 14.3255 | 198.9283 | 26.2702 | 28.0231 | 14.0792 | 196.7476 | 20.7436 | 38.1828 | 14.2975 | 197.0778 | 21.4544 | 36.0595 | 14.2167 | 198.0092 | 195.7684 | 13.4992 | 47.2037 | 6.5312 | 9.9857 | 0 | 77.3403 | 23.345 | 35.2535 | 13.6684 | 192.1843 | 195.3559 | 13.3158 | 3.1852 | 51.5485 | 79.4498 | 130.9983 | 8.3671 | 129.6763 | 91.1886 | 39.3028 | 7.9359 | 13.9376 | 194.242 | 89.9307 | 13.4913 | 0.88235 | 0.23489 | 91.8704 | 0.11817 | 0.1171 | 0.079463 | 0.094937 | 1.3444 | 0.99321
2025-06-13 12:00 | 34.9759 | 5.7344 | 0.90631 | 0.92449 | 20.8094 | 3.6976 | 13.0023 | 194.0146 | 13.8914 | 194.3182 | 24.0424 | 26.1309 | 14.319 | 198.9231 | 26.3258 | 28.0188 | 14.0777 | 196.7392 | 20.4848 | 38.3457 | 14.2923 | 197.0452 | 21.5333 | 36.3638 | 14.2219 | 197.9236 | 195.777 | 13.5026 | 47.1203 | 5.8728 | 9.9842 | 0 | 77.6219 | 23.4105 | 35.5546 | 13.6743 | 192.1953 | 195.3635 | 13.3228 | 3.6498 | 49.8479 | 79.4776 | 129.3255 | 8.2927 | 130.1163 | 91.1304 | 39.3022 | 7.8551 | 13.8914 | 194.3182 | 89.711 | 13.4291 | 0.89595 | 0.24028 | 91.6937 | 0.11673 | 0.11555 | 0.078739 | 0.093756 | 1.3671 | 0.98543
2025-06-13 13:00 | 35.064 | 8.0257 | 0.90873 | 0.92668 | 20.8019 | 3.728 | 13.0247 | 194.0286 | 13.9372 | 194.428 | 23.965 | 26.1346 | 14.3336 | 198.9405 | 26.3848 | 28.0107 | 14.0897 | 196.7334 | 20.4211 | 38.0719 | 14.2957 | 197.0199 | 21.6295 | 36.1409 | 14.232 | 198.059 | 195.8168 | 13.5186 | 47.0472 | 5.5205 | 9.9859 | 0 | 77.9028 | 23.4601 | 35.3376 | 13.6912 | 192.2136 | 195.4038 | 13.3374 | 4.161 | 49.8507 | 80.8695 | 130.7202 | 8.1432 | 129.6236 | 91.2986 | 39.3025 | 7.7117 | 13.9372 | 194.428 | 89.3445 | 13.454 | 0.89572 | 0.24256 | 92.0673 | 0.11654 | 0.11523 | 0.078787 | 0.093616 | 0.74825 | 0.3598
2025-06-13 14:00 | 35.039 | 8.649 | 0.88677 | 0.90361 | 20.2454 | 3.756 | 13.0689 | 194.2173 | 13.9729 | 194.5118 | 23.8612 | 26.1229 | 14.3515 | 199.0552 | 26.3994 | 28.0029 | 14.1107 | 196.8389 | 20.4602 | 37.6256 | 14.3241 | 197.0796 | 21.6384 | 35.7648 | 14.2519 | 198.3008 | 195.9859 | 13.5555 | 46.7234 | 5.319 | 9.9825 | 0 | 78.0935 | 23.4859 | 34.8829 | 13.7242 | 192.3409 | 195.6174 | 13.382 | 3.6192 | 52.0071 | 79.5977 | 131.6047 | 7.9207 | 128.3021 | 91.0938 | 39.3005 | 7.4979 | 13.9729 | 194.5118 | 89.5095 | 13.4525 | 0.92334 | 0.24391 | 92.0418 | 0.1148 | 0.11282 | 0.077269 | 0.092131 | 0.77134 | 0.3569
2025-06-13 15:00 | 35.086 | 7.1501 | 0.87355 | 0.88911 | 20.1026 | 3.8279 | 13.1109 | 194.3162 | 13.9006 | 194.5863 | 23.7828 | 26.1118 | 14.3722 | 199.1169 | 26.4111 | 27.9951 | 14.1336 | 196.8969 | 20.3798 | 37.8439 | 14.3592 | 197.1799 | 21.5485 | 35.7042 | 14.275 | 198.3732 | 196.0509 | 13.5879 | 46.1689 | 5.1386 | 9.9754 | 0 | 78.2434 | 23.5207 | 34.8807 | 13.7593 | 192.3493 | 195.7016 | 13.422 | 3.1901 | 52.8632 | 81.4441 | 134.3073 | 7.9492 | 129.3779 | 91.2872 | 39.3 | 7.5184 | 13.9006 | 194.5863 | 89.9763 | 13.3948 | 0.94832 | 0.25656 | 91.5167 | 0.11389 | 0.11077 | 0.076511 | 0.090559 | 0.7867 | 0.35597
2025-06-13 16:00 | 35.1048 | 5.8534 | 0.85931 | 0.87268 | 19.9988 | 3.6279 | 13.0967 | 194.289 | 13.6747 | 194.6361 | 23.6378 | 26.1113 | 14.3508 | 199.0674 | 26.4089 | 27.5686 | 14.1138 | 196.8419 | 20.432 | 38.0793 | 14.3401 | 197.1436 | 21.453 | 35.7559 | 14.2484 | 198.3364 | 196.014 | 13.5684 | 45.9364 | 4.9325 | 9.9725 | 0 | 78.3874 | 23.5423 | 34.9346 | 13.7403 | 192.3461 | 195.6503 | 13.4069 | 3.2534 | 51.0627 | 76.2941 | 127.3568 | 7.7135 | 128.4315 | 91.1514 | 39.2981 | 7.2912 | 13.6747 | 194.6361 | 89.6752 | 13.1787 | 0.96179 | 0.26209 | 91.0952 | 0.11261 | 0.11078 | 0.074724 | 0.089233 | 0.80261 | 0.35645
2025-06-13 17:00 | 34.5415 | 7.2656 | 0.82282 | 0.84071 | 19.1769 | 3.9988 | 13.0745 | 194.1813 | 14.0589 | 194.6611 | 22.9541 | 25.0273 | 14.2248 | 198.6106 | 26.3892 | 27.0712 | 14.0386 | 196.6063 | 20.3809 | 38.5427 | 14.2752 | 196.9283 | 21.4817 | 36.7896 | 14.2024 | 198.125 | 195.7785 | 13.5009 | 43.7502 | 4.7491 | 9.9722 | 0 | 78.4431 | 23.5397 | 35.4611 | 13.6927 | 192.1997 | 195.5329 | 13.3771 | 3.2419 | 50.2466 | 87.8779 | 138.1245 | 8.6481 | 135.4634 | 90.7954 | 39.2949 | 8.1713 | 14.0589 | 194.6611 | 89.971 | 13.5628 | 0.97241 | 0.26684 | 92.2171 | 0.10987 | 0.11518 | 0.071633 | 0.087332 | 0.83822 | 0.35775
2025-06-13 18:00 | 34.3222 | 9.3972 | 0.8061 | 0.82276 | 18.2555 | 4.5492 | 12.9678 | 193.8161 | 14.5252 | 194.4788 | 22.0538 | 24.0067 | 14.0307 | 197.9719 | 26.4275 | 26.997 | 13.8982 | 196.208 | 20.3948 | 39.0302 | 14.1625 | 196.6142 | 21.5874 | 37.8187 | 14.096 | 197.6654 | 195.3136 | 13.3582 | 41.9671 | 4.6175 | 9.9715 | 0 | 78.4635 | 23.5288 | 36.4852 | 13.5752 | 191.8432 | 195.1875 | 13.2669 | 3.2509 | 50.1173 | 106.0202 | 156.1376 | 10.1182 | 144.2059 | 91.6806 | 39.2887 | 9.5737 | 14.5252 | 194.4788 | 91.2494 | 14.0577 | 0.9831 | 0.27512 | 93.2984 | 0.10811 | 0.12606 | 0.069967 | 0.085775 | 0.85903 | 0.36112
2025-06-13 19:00 | 34.7581 | 9.0835 | 0.80389 | 0.81455 | 17.5313 | 4.4496 | 12.9505 | 193.8203 | 14.522 | 194.3368 | 22.3843 | 24.0791 | 14.0228 | 198.0567 | 26.4159 | 26.997 | 13.8874 | 196.2177 | 20.2898 | 38.9296 | 14.1565 | 196.5885 | 21.4866 | 37.8835 | 14.0818 | 197.6066 | 195.3403 | 13.3473 | 42.4148 | 4.5041 | 9.9702 | 0 | 78.4849 | 23.5057 | 36.9392 | 13.5608 | 191.8193 | 195.1935 | 13.2538 | 3.91 | 48.5479 | 106.1122 | 154.6601 | 10.3691 | 143.7753 | 92.6355 | 39.2698 | 9.8262 | 14.522 | 194.3368 | 91.6629 | 14.0567 | 0.98651 | 0.27738 | 92.6473 | 0.10741 | 0.13785 | 0.069133 | 0.084901 | 0.86098 | 0.36215
2025-06-13 20:00 | 34.9898 | 7.8587 | 0.79598 | 0.80643 | 17.2183 | 4.4314 | 12.9389 | 193.7562 | 14.5174 | 194.327 | 23.6619 | 24.0834 | 14.0533 | 198.1808 | 26.3577 | 26.9979 | 13.892 | 196.198 | 19.9576 | 39.0531 | 14.163 | 196.5262 | 21.2301 | 38.1998 | 14.0833 | 197.6464 | 195.3127 | 13.346 | 42.9759 | 4.4478 | 9.9688 | 0 | 78.4786 | 23.4875 | 37.1692 | 13.5528 | 191.7492 | 195.1365 | 13.2447 | 3.9503 | 49.9641 | 105.091 | 155.0551 | 10.3667 | 143.6293 | 92.3993 | 39.2555 | 9.8242 | 14.5174 | 194.327 | 91.2833 | 14.0609 | 0.98474 | 0.27341 | 92.7667 | 0.1072 | 0.14375 | 0.068858 | 0.08459 | 0.85641 | 0.36024
2025-06-13 21:00 | 35.1894 | 6.1933 | 0.79625 | 0.80492 | 17.2249 | 4.3288 | 12.9804 | 193.8972 | 14.5192 | 194.4091 | 24.7483 | 24.0846 | 14.1233 | 198.4336 | 26.3716 | 26.67 | 13.9417 | 196.3586 | 20.0474 | 38.5707 | 14.2054 | 196.6696 | 21.1928 | 37.5157 | 14.1212 | 197.7783 | 195.4856 | 13.3978 | 43.4228 | 4.4284 | 9.9695 | 0 | 78.4797 | 23.4891 | 36.5819 | 13.5968 | 191.8714 | 195.2862 | 13.2878 | 3.4028 | 51.2872 | 101.0405 | 152.3277 | 10.0067 | 141.1332 | 92.1602 | 39.2551 | 9.4831 | 14.5192 | 194.4091 | 91.2321 | 14.0655 | 0.98439 | 0.27125 | 92.2094 | 0.10716 | 0.14456 | 0.068825 | 0.084561 | 0.85493 | 0.35944
2025-06-13 22:00 | 35.1104 | 5.5634 | 0.79363 | 0.80308 | 17.4522 | 4.0572 | 13.1527 | 194.4482 | 14.6935 | 194.5315 | 25.6633 | 24.0834 | 14.295 | 198.9719 | 26.4217 | 26.1664 | 14.0969 | 196.8243 | 20.0502 | 37.7025 | 14.3339 | 197.0717 | 21.2631 | 36.2997 | 14.2559 | 198.2057 | 196.0386 | 13.5752 | 43.7065 | 4.5682 | 9.9696 | 0 | 78.5219 | 23.506 | 35.5692 | 13.7618 | 192.2807 | 195.8083 | 13.4582 | 3.0087 | 50.581 | 91.8676 | 142.4486 | 9.057 | 132.0216 | 92.1038 | 39.2552 | 8.5753 | 14.6935 | 194.5315 | 90.5307 | 14.2332 | 0.98507 | 0.27258 | 90.544 | 0.10731 | 0.14402 | 0.068944 | 0.63326 | 0.85078 | 0.35884
2025-06-13 23:00 | 33.9801 | 6.0293 | 0.78553 | 0.79831 | 17.6979 | 3.3711 | 13.1045 | 194.4237 | 13.9512 | 193.6151 | 26.1445 | 24.0813 | 14.2559 | 198.9067 | 26.3426 | 25.3614 | 14.0585 | 196.6709 | 19.7946 | 36.7564 | 14.2608 | 197.0265 | 21.1728 | 35.4522 | 14.1972 | 198.0333 | 195.9675 | 13.5412 | 44.5079 | 4.7886 | 9.9703 | 0 | 78.5901 | 23.5334 | 34.6063 | 13.7269 | 192.2629 | 195.7342 | 13.4189 | 3.4229 | 50.1422 | 64.4091 | 114.5513 | 7.9564 | 124.0691 | 91.2218 | 34.9018 | 7.2076 | 13.9512 | 193.6151 | 89.6431 | 13.4896 | 0.98254 | 0.27188 | 90.7098 | 0.10747 | 0.14312 | 0.06903 | 0.63362 | 3.1477 | 2.6832
2025-06-14 | 35.3205 | 6.4414 | 0.83736 | 0.85194 | 17.9404 | 3.7815 | 13.0236 | 194.0965 | 14.404 | 193.2513 | 25.9454 | 24.0801 | 14.2246 | 198.959 | 26.3223 | 25.7208 | 14.0459 | 196.7886 | 19.1343 | 38.4343 | 14.2457 | 196.8963 | 20.1646 | 39.6245 | 14.2039 | 198.1697 | 195.8618 | 13.4938 | 46.5586 | 4.9448 | 9.9728 | 0 | 78.6768 | 23.5506 | 37.6966 | 13.6502 | 192.0694 | 195.4594 | 13.3451 | 3.0295 | 50.1319 | 83.4316 | 133.5635 | 8.7177 | 133.691 | 89.0432 | 24.9014 | 7.0808 | 14.404 | 193.2513 | 86.142 | 13.8584 | 0.9881 | 0.2693 | 85.7753 | 0.10779 | 0.14346 | 0.068649 | 0.084745 | 1.161 | 0.68206
Total | MW: 829.5654; MVAR: 173.5335; kg/s: 3842476.9283; kg/s: 323884.8703; kg/s: 4249782.3328; kg/s: 7631450.4758; kg/s: 11881232.8086; kg/s: 11528116.9087
Average | 34.5652 | 7.2306 | 0.84439 | 0.85949 | 18.8618 | 3.9801 | 13.1208 | 194.3934 | 14.2781 | 194.5952 | 23.7213 | 25.9791 | 14.3043 | 198.9645 | 25.9376 | 27.2405 | 14.0962 | 196.8405 | 20.638 | 37.2029 | 14.313 | 197.1809 | 21.4043 | 36.2119 | 14.2456 | 198.1294 | 196.0009 | 13.5602 | 44.4731 | 5.9387 | 9.9746 | 0 | 77.2814 | 22.956 | 37.3608 | 13.756 | 192.3541 | 195.7523 | 13.4314 | 3.7487 | 49.1873 | 88.327 | 137.5143 | 9.0316 | 133.4273 | 91.4633 | 42.5782 | 8.5976 | 14.2781 | 194.5952 | 89.9808 | 13.7245 | 0.9718 | 0.29 | 91.73 | 0.17337 | 0.12826 | 0.072573 | 0.24944 | 1.3086 | 0.85904
Min | 32.0642 | 5.5634 | 0.78553 | 0.79831 | 17.2183 | 3.3711 | 12.9389 | 193.7562 | 13.6747 | 193.2513 | 20.9253 | 24.0067 | 14.0228 | 197.9719 | 23.2992 | 25.3614 | 13.8874 | 196.198 | 19.1343 | 33.0412 | 14.1565 | 196.5262 | 20.1646 | 33.3287 | 14.0818 | 197.6066 | 195.3127 | 13.346 | 39.4586 | 4.4284 | 9.9668 | 0 | 75.424 | 21.2203 | 34.6063 | 13.5528 | 191.7492 | 195.1365 | 13.2447 | 2.4869 | 41.9902 | 64.4091 | 114.5513 | 7.7135 | 123.2319 | 89.0432 | 24.9014 | 7.0808 | 13.6747 | 193.2513 | 86.142 | 13.1787 | 0.87133 | 0.23489 | 85.7753 | 0.10716 | 0.11077 | 0.068649 | 0.084561 | 0.72999 | 0.35597
Max | 35.3205 | 9.3972 | 0.91859 | 0.94389 | 21.5247 | 4.5492 | 13.6054 | 196.0447 | 14.9018 | 195.9074 | 26.1445 | 33.5796 | 14.7472 | 200.5155 | 26.4275 | 30.2887 | 14.5198 | 198.2476 | 21.9013 | 39.0531 | 14.6508 | 198.4193 | 21.7463 | 39.6245 | 14.6217 | 199.3156 | 197.5474 | 14.0267 | 47.2037 | 7.6379 | 9.9859 | 0 | 78.6768 | 23.5506 | 52.2149 | 14.2119 | 193.6345 | 197.3231 | 13.9162 | 6.6617 | 54.1868 | 106.1122 | 156.1376 | 10.7502 | 144.2059 | 92.6355 | 49.7765 | 10.5062 | 14.9018 | 195.9074 | 91.6629 | 14.2332 | 1.037 | 0.34735 | 93.2984 | 0.86059 | 0.1478 | 0.0798 | 1.1504 | 3.1477 | 2.6832

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1
18 |  | Night | 22:15 | 5.55 | 22.2
19 | 2025-06-10 | Day | 8:55 | 5.69 | 31.6
20 |  | Night | 0:20 | 5.18 | 24.3
21 | 2025-06-11 | Day | 17:00 | 5.07 | 21.6
22 |  | Night | 22:30 | 5.62 | 28.8
23 | 2025-06-12 | Day | 10:10 | 5.08 | 27.3
24 |  | Night | 21:30 | 5.64 | 26.6
25 | 2025-06-13 | Day | 8:40 | 5.11 | 27.1
26 |  | Night | 22:00 | 5.77 | 25.5
27 | 2025-06-14 | Day
28 |  | Night
29 | 2025-06-15 | Day
30 |  | Night
31 | 2025-06-16 | Day
32 |  | Night
33 | 2025-06-17 | Day
34 |  | Night
35 | 2025-06-18 | Day
36 |  | Night
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-13
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0