## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-14
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 25.3688 | 198.6051 | 20.947
|  | #6-2 | Production | 27.8589 | 196.7337 | 20.6327
|  | #6-3 | Production | 20.1344 | 196.9665 | 38.4754
|  | #6-4 | Production | 20.9816 | 197.9434 | 39.1072
|  | #8-1 | Shut in | 4.8779 | 80.5192 | 9.9754
|  | #8-2 | Production | 23.2151 | 192.3987 | 38.9082
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 43.5726 | 3764673.2295
|  | PAD #8 - STEAM |  |  |  |  | 3.244 | 280280.7473 | Online
|  | BRINE HEADER |  |  |  |  | 79.1397 | 6837670.5781 | Offline
|  | TOTAL FLOW |  |  |  |  | 125.9563 | 10882624.5549
|  | PRESS SEPARATOR IJN 6 | Online | 13.508 | 195.8259
|  | PRESS SEPARATOR IJN 8 | Online | 13.4034 | 195.6526
| INJECTION WELL | #5-1 | Injection | 6.9763 | 91.4391 | 19.8602 | 131.3994 | 11352910.8002
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 33.9234 |  |  | 814.1613
|  | NET | 31.3417 |  |  | 752.2012
| PARASITIC LOAD |  | 2.5817 |  |  | 61.9601
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 3.713 |  |  | 13366.6684
|  | NET | 4.0188 |  |  | 14467.7036
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-14
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 752201.2383 |  | 0 |  | 752201.2383
|  |  |  | 752201.2383 |  | 0 |  | 752201.2383
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 752660 | [7 empty] | 752660
M-T-D GROSS GENERATION (kWHR) |  |  |  | 11583425 | [7 empty] | 11583425
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18163.31 | 0 | 3389.16 | 46.3 | 743 | 786 | 23127.77
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 256194.44 | -283254.3 | 76325.38 | 610.3 | 17539 | 20729 | 115203.68
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 33.9234 |  |  | 5.7144 |  | 19.4515
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 336
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 90.86%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 3764.6732 |  | 280.2807 |  |  | 4202.8814
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.043573 |  | 0.003244 |  |  | 0.048644
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 6837.6706
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.07914
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 11040.5519
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.12778
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 194.2638 |  |  |  | 194.3964
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 13.089 |  |  |  | 14.1469
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 17.8848 |  | 21.8146 |  |  | 19.4515
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [14 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [13 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:01 | PLN adviced load ROH 31.05 MW (Mr. Triashfi Al Mutaqobili)
0:30 | Turn off ACC Fan side CCW - F9357
0:32 | Turn off ACC Fan side CW - F9313
7:00 | Update abnormal operation of CW ACC Fan -> priority high : F9305, F9313, F9310
7:10 | Update abnormal operation of CCW ACC Fan -> priority high : F9351, F9367, F9368, F9370
7:45 | Handover night shift to day shift
8:45 | Daily Toolbox meeting and safety talk
10:21 | Change over Generator Cooling water pump P9813B to P9813A. Before 3.25 barg / 25C, After 3.17 barg / 25C [Standard Activity]
10:26 | ACC Fan F9313 switch to auto mode but can't run. Switch to manual mode and run manually.
10:28 | ACC Fan F9357 switch to auto mode and run automatically
10:36 | Switch lead condensate pump A to B. Mechseal pressure 11.5 barg / oil level 100% / discharge pressure 18.9 barg [Standard activity]
11:00 | Dump valve A IJN 8 (LV2327A) offline exercise and switch priority from B to A. [Standard activity]
11:28 | Running Test Standby Reinjection pump P2601B [Standard activity]
11:37 | Running Test Standby Brine Booster Pump B IJN 6 (P2201A). On 400rpm mechseal pressure drop from 6 barg to 1 barg. [Standard activity]
15:00 | pH Check and Release Dispossal Pond. Result: 8.77 pH / 22.8C [Standard activity]
22:00 | Update pH brine+condensate inlet preheater (pH : 5.78 and Temperature : 28.9 degC)
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Hary |  |  |  | CCR Operator : Fauzan |  |  |  | Steamfield : Vandy
Night Shift | Shift Leader : Arbima |  |  |  | CCR Operator : Dwiki |  |  |  | Steamfield : Rafly
22
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-14
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2189100 | 2192200 | 3100 | 64350
(BACKUP) |  | 2126290 | 2187470 | 2190560 | 3090 | 64270
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 103002790 | 103755450 | 752660 | 10653540
(BACKUP) |  | 93082960 | 102981030 | 103733480 | 752450 | 10650520
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4615050 | 4647420 | 32370 | 505190
(BACKUP) |  | 4144060 | 4617010 | 4649390 | 32380 | 505330
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 112090492 | 112906680 | 816188 | 11583425
TOTAL |  |  |  |  | 816188 | 11583425
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 18416276 | 18555179 | 138903 | 2024924
TOTAL |  |  |  |  | 138903 | 2024924
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3327349.47 | 3345512.78 | 18163.31 | 256194.44
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1062694.63 | 1066083.79 | 3389.16 | 76325.38
U Ijen 5 |  | 7258.6 | 7822.6 | 7868.9 | 46.3 | 610.3
U Ijen 6 |  | 247889 | 264685 | 265428 | 743 | 17539
U Ijen 8 |  | 299837 | 319780 | 320566 | 786 | 20729
TOTAL |  |  |  |  | 23127.77 | 371398.12
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-14 01:00 | 34.156 | 5.1719 | 0.80832 | 0.82228 | 17.8848 | 3.2109 | 13.0847 | 194.2763 | 13.6394 | 193.954 | 25.6437 | 24.0846 | 14.218 | 198.8446 | 26.2406 | 23.8187 | 14.0418 | 196.9023 | 20.4728 | 35.2773 | 14.2366 | 196.9473 | 21.3708 | 35.0334 | 14.1703 | 198.0513 | 195.886 | 13.5259 | 44.784 | 4.8686 | 9.9719 | 0 | 78.7339 | 23.61 | 33.7708 | 13.693 | 192.1468 | 195.6194 | 13.3951 | 3.876 | 45.9442 | 63.729 | 109.6732 | 8.268 | 126.8921 | 90.3389 | 24.5521 | 6.764 | 13.6394 | 193.954 | 88.9519 | 13.1658 | 0.98613 | 0.26931 | 91.17 | 0.10718 | 0.1461 | 0.068756 | 0.08474 | 1.5462 | 1.0507
2025-06-14 02:00 | 34.1144 | 3.7271 | 0.81482 | 0.82645 | 18.0603 | 3.1556 | 13.0684 | 194.193 | 13.4353 | 193.9804 | 25.4033 | 24.0852 | 14.172 | 198.713 | 26.313 | 23.0947 | 13.9949 | 196.8784 | 20.4174 | 34.7161 | 14.1776 | 196.6599 | 21.7255 | 34.2413 | 14.118 | 197.8144 | 195.8113 | 13.4995 | 44.4569 | 4.6938 | 9.9696 | 0 | 78.8041 | 23.6834 | 33.3437 | 13.6721 | 192.1071 | 195.5404 | 13.3747 | 3.5236 | 46.4259 | 61.2258 | 107.6517 | 7.9308 | 125.2042 | 90.3388 | 24.5521 | 6.4664 | 13.4353 | 193.9804 | 88.9949 | 12.9562 | 0.98351 | 0.27274 | 90.9329 | 0.10727 | 0.14441 | 0.068775 | 0.084709 | 0.90341 | 0.40022
2025-06-14 03:00 | 33.9189 | 3.1427 | 0.8292 | 0.83826 | 18.618 | 3.207 | 13.013 | 194.0215 | 13.4173 | 193.9419 | 25.2108 | 24.0822 | 14.1206 | 198.5562 | 26.3681 | 23.003 | 13.9434 | 196.6984 | 20.5834 | 34.6859 | 14.1226 | 196.4375 | 21.7724 | 34.2037 | 14.0642 | 197.4789 | 195.6495 | 13.4441 | 44.1906 | 4.5319 | 9.971 | 0 | 78.8931 | 23.7255 | 33.3331 | 13.6236 | 192.023 | 195.3901 | 13.3211 | 2.7741 | 45.7118 | 63.0651 | 108.7769 | 7.8433 | 125.5039 | 90.4626 | 24.5527 | 6.3632 | 13.4173 | 193.9419 | 88.9204 | 12.9372 | 0.97711 | 0.27975 | 90.9342 | 0.10759 | 0.13721 | 0.068976 | 0.084923 | 0.89918 | 0.39972
2025-06-14 04:00 | 33.955 | 4.1515 | 0.82258 | 0.83202 | 18.7628 | 3.1413 | 13.0744 | 194.1905 | 13.405 | 193.9225 | 25.0725 | 24.0812 | 14.1762 | 198.7022 | 26.4201 | 23.0026 | 14.0004 | 196.8044 | 20.8117 | 34.473 | 14.18 | 196.5859 | 21.8051 | 34.1009 | 14.1191 | 197.5858 | 195.8092 | 13.5031 | 43.9347 | 4.4103 | 9.9727 | 0 | 78.9883 | 23.7661 | 32.9266 | 13.681 | 192.0998 | 195.5475 | 13.3801 | 2.9779 | 45.0942 | 61.5671 | 106.6613 | 7.7585 | 125.6293 | 90.6243 | 24.553 | 6.2727 | 13.405 | 193.9225 | 89.257 | 12.9131 | 0.97291 | 0.27469 | 91.0757 | 0.10763 | 0.13493 | 0.069014 | 0.084961 | 0.89612 | 0.39851
2025-06-14 05:00 | 33.697 | 5.8147 | 0.79747 | 0.81045 | 18.5332 | 3.0992 | 13.0687 | 194.1916 | 13.3771 | 193.7434 | 24.621 | 24.0807 | 14.141 | 198.5741 | 26.4559 | 22.9911 | 13.9744 | 196.7361 | 20.7534 | 34.0275 | 14.1498 | 196.496 | 21.9655 | 33.9342 | 14.0893 | 197.569 | 195.7678 | 13.4839 | 43.2454 | 4.3094 | 9.9724 | 0 | 79.0513 | 23.8034 | 32.1635 | 13.6719 | 192.0781 | 195.5441 | 13.3714 | 3.1107 | 46.1798 | 58.2536 | 104.4334 | 7.6714 | 125.7735 | 89.9765 | 24.5525 | 6.1802 | 13.3771 | 193.7434 | 88.9918 | 12.8742 | 0.9756 | 0.26944 | 90.6189 | 0.10724 | 0.14059 | 0.068803 | 0.084602 | 0.89895 | 0.39754
2025-06-14 06:00 | 33.3562 | 6.5676 | 0.80376 | 0.81776 | 19.1096 | 3.5464 | 13.0539 | 194.146 | 13.6576 | 193.8118 | 24.8312 | 23.4423 | 14.1152 | 198.484 | 26.5204 | 22.6106 | 13.9488 | 196.6866 | 20.6559 | 33.9622 | 14.1145 | 196.4379 | 21.8922 | 33.9046 | 14.069 | 197.524 | 195.6803 | 13.4573 | 42.5635 | 4.324 | 9.9725 | 0 | 79.1245 | 23.8298 | 32.2621 | 13.6651 | 192.0879 | 195.5097 | 13.3563 | 2.8868 | 49.8448 | 68.4483 | 118.293 | 8.0696 | 128.7425 | 90.5569 | 24.5528 | 6.5053 | 13.6576 | 193.8118 | 89.361 | 13.1289 | 0.96918 | 0.27973 | 91.1732 | 0.10768 | 0.14029 | 0.069417 | 0.085688 | 0.89802 | 0.40234
2025-06-14 07:00 | 33.5254 | 6.0641 | 0.84143 | 0.85612 | 19.963 | 4.0005 | 13.1016 | 194.2881 | 13.9578 | 194.3701 | 25.3086 | 22.4587 | 14.1855 | 198.7129 | 26.6299 | 22.1311 | 14.0073 | 196.8939 | 20.9032 | 34.3969 | 14.1571 | 196.6151 | 21.8549 | 34.151 | 14.1433 | 197.6855 | 195.8404 | 13.514 | 43.2665 | 4.3934 | 9.9779 | 0 | 79.3699 | 23.8501 | 32.7799 | 13.7283 | 192.3258 | 195.6269 | 13.4055 | 3.2918 | 53.8162 | 80.3007 | 134.1169 | 8.1965 | 129.4488 | 91.307 | 24.5569 | 6.629 | 13.9578 | 194.3701 | 89.9081 | 13.3952 | 0.93058 | 0.28503 | 92.1694 | 0.11092 | 0.12401 | 0.072187 | 0.089343 | 0.86987 | 0.40209
2025-06-14 08:00 | 33.5134 | 6.0111 | 0.87599 | 0.89197 | 20.3128 | 3.9602 | 13.313 | 195.0121 | 14.1858 | 194.9985 | 25.2357 | 21.9869 | 14.4589 | 199.4578 | 26.7492 | 21.984 | 14.2696 | 197.672 | 21.2737 | 36.4159 | 14.4353 | 197.5 | 21.8452 | 36.1874 | 14.4335 | 198.6305 | 196.5586 | 13.744 | 44.521 | 4.3301 | 9.9799 | 0 | 79.7955 | 23.8713 | 33.8312 | 13.9547 | 193.0112 | 196.2871 | 13.6197 | 3.3985 | 50.3985 | 82.321 | 132.7196 | 8.3696 | 130.804 | 91.1403 | 24.5623 | 6.777 | 14.1858 | 194.9985 | 90.3736 | 13.5946 | 0.86938 | 0.27146 | 92.7021 | 0.11445 | 0.11464 | 0.075609 | 0.09292 | 1.4454 | 4.2016
2025-06-14 09:00 | 33.5028 | 6.4052 | 0.89878 | 0.91633 | 20.6942 | 3.5094 | 13.5372 | 195.7763 | 14.1115 | 195.8335 | 25.074 | 21.38 | 14.6977 | 200.1125 | 26.9352 | 21.3672 | 14.5128 | 198.4111 | 21.2639 | 37.8364 | 14.7029 | 198.3249 | 21.8954 | 37.8296 | 14.7031 | 199.671 | 197.3104 | 13.9752 | 44.7306 | 4.5101 | 9.9789 | 0 | 80.2381 | 23.8884 | 35.0721 | 14.1799 | 193.7353 | 197.0177 | 13.8377 | 2.9979 | 46.02 | 71.5538 | 117.5739 | 8.2507 | 129.8092 | 91.8753 | 24.5659 | 6.6829 | 14.1115 | 195.8335 | 90.7426 | 13.5153 | 0.8275 | 0.23669 | 91.8482 | 0.11642 | 0.11724 | 0.077579 | 0.094482 | 1.2906 | 6.3753
2025-06-14 10:00 | 33.8337 | 6.3949 | 0.91605 | 0.93453 | 21.2344 | 3.6525 | 13.4819 | 195.5573 | 14.1898 | 195.7441 | 25.3114 | 20.2113 | 14.6239 | 199.834 | 27.1705 | 20.3495 | 14.4423 | 198.2133 | 20.7842 | 38.1419 | 14.6489 | 198.2059 | 21.8158 | 39.1433 | 14.6584 | 199.5954 | 197.1116 | 13.9147 | 44.0259 | 4.884 | 9.9813 | 0 | 80.5576 | 23.7829 | 36.5681 | 14.1556 | 193.6638 | 196.8678 | 13.787 | 3.4862 | 48.3646 | 75.2116 | 123.5762 | 8.4654 | 131.1635 | 91.8393 | 24.566 | 6.8627 | 14.1898 | 195.7441 | 91.3145 | 13.5904 | 0.82473 | 0.22022 | 91.6116 | 0.11668 | 0.11705 | 0.097517 | 2.7481 | 0.5283 | 4.4328
2025-06-14 11:00 | 34.054 | 6.1289 | 0.92937 | 0.94973 | 21.8146 | 4.0299 | 13.4279 | 195.3554 | 14.4142 | 195.3017 | 26.0405 | 19.3369 | 14.5903 | 199.6817 | 27.4228 | 19.47 | 14.3936 | 198.0389 | 20.4655 | 38.6972 | 14.63 | 198.1547 | 21.4734 | 40.0242 | 14.6119 | 199.4262 | 196.9318 | 13.8664 | 43.9686 | 4.9921 | 9.9845 | 0 | 80.8403 | 23.5205 | 37.4095 | 14.1359 | 193.5433 | 196.7388 | 13.7444 | 3.4047 | 49.5886 | 87.6463 | 137.2349 | 8.7803 | 133.1535 | 91.8027 | 24.5666 | 7.1298 | 14.4142 | 195.3017 | 91.5342 | 13.8036 | 0.81379 | 0.22002 | 91.7222 | 0.11761 | 0.11689 | 2.1554 | 2.7493 | 0.49108 | 3.7308
2025-06-14 12:00 | 34.1725 | 5.5841 | 0.92987 | 0.95272 | 21.7557 | 3.8235 | 13.3937 | 195.2635 | 14.3189 | 195.2328 | 26.4028 | 18.6552 | 14.5748 | 199.6548 | 27.7077 | 18.5463 | 14.3732 | 197.9677 | 20.487 | 39.2377 | 14.6218 | 198.0759 | 21.0703 | 40.8393 | 14.5818 | 199.2656 | 196.8887 | 13.8481 | 44.6788 | 4.9579 | 9.9882 | 0 | 81.1439 | 23.2998 | 37.2441 | 14.0991 | 193.5068 | 196.6798 | 13.7097 | 2.8925 | 49.5361 | 81.1211 | 130.6572 | 8.3089 | 130.351 | 91.856 | 24.5681 | 6.7271 | 14.3189 | 195.2328 | 90.6672 | 13.7379 | 0.8021 | 0.20966 | 91.3015 | 0.11923 | 0.11828 | 2.138 | 0.094018 | 0.46492 | 3.5731
2025-06-14 13:00 | 34.2933 | 5.6057 | 0.91035 | 0.93264 | 21.0765 | 3.331 | 13.5678 | 195.8416 | 14.1123 | 195.0986 | 26.7505 | 17.1466 | 14.7343 | 200.147 | 28.083 | 17.0441 | 14.5339 | 198.3521 | 20.0768 | 40.3743 | 14.7831 | 198.4978 | 20.711 | 44.625 | 14.7845 | 199.8304 | 197.4541 | 14.0214 | 45.1824 | 4.8227 | 9.9894 | 0 | 81.3685 | 23.2129 | 36.2727 | 14.2494 | 193.9268 | 197.2133 | 13.8773 | 2.8258 | 49.0268 | 65.2033 | 114.2301 | 8.1716 | 129.8332 | 91.3095 | 24.5661 | 6.5968 | 14.1123 | 195.0986 | 90.3955 | 13.5044 | 0.82449 | 0.20738 | 91.6415 | 0.1184 | 0.11714 | 0.079219 | 0.093278 | 0.48636 | 5.2499
2025-06-14 14:00 | 34.3491 | 5.7558 | 0.8603 | 0.88166 | 19.8298 | 3.018 | 13.6533 | 196.1875 | 14.0834 | 195.7154 | 26.6407 | 15.7452 | 14.7848 | 200.3442 | 28.4764 | 15.9001 | 14.5884 | 198.4174 | 19.8982 | 42.6745 | 14.8981 | 198.8818 | 20.2934 | 45.8207 | 14.8498 | 200.0852 | 197.7654 | 14.0973 | 45.1907 | 4.6519 | 9.9838 | 0 | 81.4933 | 23.1823 | 36.385 | 14.3114 | 194.1955 | 197.5219 | 13.958 | 3.0612 | 48.9363 | 54.7292 | 103.6654 | 8.3474 | 128.0012 | 91.4171 | 23.599 | 6.4251 | 14.0834 | 195.7154 | 90.1304 | 13.4356 | 0.86874 | 0.20835 | 91.2549 | 0.11503 | 0.11407 | 0.07656 | 0.091302 | 0.53067 | 6.4329
2025-06-14 15:00 | 33.8548 | 4.7831 | 0.81253 | 0.8297 | 18.7083 | 3.5835 | 13.0837 | 194.275 | 14.5846 | 194.8209 | 25.2952 | 17.538 | 14.1658 | 198.4161 | 28.6887 | 16.9875 | 13.9797 | 196.5023 | 19.6787 | 41.9425 | 14.3157 | 197.2155 | 20.0503 | 43.497 | 14.2221 | 198.0059 | 195.8167 | 13.5002 | 43.7299 | 4.6278 | 9.9741 | 0 | 81.4596 | 23.0843 | 42.2948 | 13.7691 | 192.5931 | 195.6948 | 13.405 | 3.5158 | 48.9901 | 72.33 | 121.3201 | 10.6604 | 127.6588 | 90.8809 | 17.7641 | 6.3135 | 14.5846 | 194.8209 | 89.8113 | 14.092 | 0.9141 | 0.23511 | 90.7488 | 0.11069 | 0.11298 | 4.267 | 0.088346 | 0.58167 | 3.2965
2025-06-14 16:00 | 33.2303 | 5.5773 | 0.78978 | 0.8029 | 18.3755 | 4.1989 | 12.6183 | 192.6445 | 14.6784 | 193.3158 | 23.5428 | 19.8727 | 13.6384 | 196.742 | 28.8063 | 18.7263 | 13.4711 | 194.8682 | 19.2036 | 40.228 | 13.7958 | 195.8388 | 20.063 | 42.7559 | 13.7349 | 196.4024 | 194.1224 | 12.9995 | 41.8716 | 4.7929 | 9.9721 | 0 | 81.358 | 22.8571 | 47.6527 | 13.3216 | 191.133 | 194.1061 | 12.9498 | 3.5355 | 48.2099 | 91.3196 | 139.5295 | 10.803 | 131.7035 | 90.5598 | 12.8919 | 6.7072 | 14.6784 | 193.3158 | 90.2175 | 14.3054 | 0.93211 | 0.26018 | 91.2843 | 0.85227 | 0.11575 | 7.0629 | 0.086722 | 0.60951 | 0.41624
2025-06-14 17:00 | 33.1973 | 8.0762 | 0.77683 | 0.79008 | 18.3663 | 4.3663 | 12.6435 | 192.7437 | 14.5181 | 193.4657 | 22.7434 | 20.0616 | 13.6209 | 196.7208 | 28.9307 | 19.4874 | 13.4708 | 194.8621 | 19.5138 | 40.4276 | 13.8135 | 195.9098 | 20.0896 | 41.5979 | 13.7192 | 196.3354 | 194.1792 | 13.0094 | 41.1024 | 4.9686 | 9.9715 | 0 | 81.3055 | 22.6411 | 47.4974 | 13.3251 | 191.1293 | 194.1798 | 12.9668 | 3.3109 | 47.2972 | 97.653 | 144.9502 | 8.934 | 135.9997 | 91.2187 | 12.8915 | 7.3743 | 14.5181 | 193.4657 | 91.2778 | 14.0929 | 0.93748 | 0.25828 | 92.3537 | 1.0507 | 0.12334 | 4.5378 | 0.086395 | 0.61722 | 0.41463
2025-06-14 18:00 | 33.5086 | 7.7838 | 0.7795 | 0.79549 | 18.4937 | 4.3957 | 12.7235 | 192.9977 | 14.5756 | 193.7171 | 23.1831 | 20.5604 | 13.7154 | 197.0416 | 29.0534 | 20.2411 | 13.5667 | 195.1993 | 19.5479 | 40.8016 | 13.9048 | 195.9321 | 20.1675 | 41.1612 | 13.8006 | 196.4574 | 194.4409 | 13.093 | 41.2665 | 5.0321 | 9.97 | 0 | 81.2876 | 22.5457 | 46.9558 | 13.3966 | 191.3062 | 194.4222 | 13.0437 | 3.4179 | 47.0642 | 100.2297 | 147.2939 | 9.1847 | 138.407 | 91.7432 | 12.8913 | 7.8287 | 14.5756 | 193.7171 | 92.0743 | 14.1019 | 0.9418 | 0.2563 | 92.7539 | 0.30673 | 0.12928 | 5.365 | 0.086314 | 0.61969 | 0.41465
2025-06-14 19:00 | 33.9222 | 6.6011 | 0.79511 | 0.81268 | 18.7349 | 4.3777 | 12.8236 | 193.3706 | 14.6399 | 193.9199 | 24.3202 | 21.022 | 13.8621 | 197.5693 | 29.1469 | 20.748 | 13.6997 | 195.6673 | 19.3983 | 41.0837 | 14.0274 | 196.2715 | 20.2911 | 41.3743 | 13.9405 | 196.9661 | 194.851 | 13.2077 | 41.8505 | 5.0615 | 9.9717 | 0 | 81.3162 | 22.5145 | 45.5496 | 13.496 | 191.6323 | 194.8119 | 13.145 | 3.3966 | 47.9 | 100.6018 | 148.5018 | 9.5241 | 139.9452 | 92.6423 | 12.8908 | 8.1414 | 14.6399 | 193.9199 | 91.924 | 14.107 | 0.94293 | 0.25681 | 92.0986 | 0.10849 | 0.13076 | 5.6233 | 0.086369 | 0.6144 | 0.41571
2025-06-14 20:00 | 34.061 | 6.2759 | 0.81252 | 0.82961 | 19.2243 | 4.3409 | 12.8472 | 193.487 | 14.6551 | 194.1347 | 25.3257 | 21.0213 | 13.9167 | 197.7996 | 29.2147 | 20.7373 | 13.7382 | 195.8262 | 19.4658 | 40.838 | 14.0561 | 196.3454 | 20.379 | 40.85 | 13.9775 | 197.3272 | 195.0169 | 13.2459 | 42.4921 | 5.1583 | 9.9722 | 0 | 81.3633 | 22.5068 | 44.5505 | 13.5209 | 191.796 | 194.9536 | 13.1706 | 3.2524 | 49.1694 | 98.6855 | 147.8549 | 9.5959 | 139.6841 | 92.6261 | 12.8901 | 8.2159 | 14.6551 | 194.1347 | 91.4548 | 14.0988 | 0.93543 | 0.26089 | 92.4883 | 0.10872 | 0.12951 | 3.5147 | 0.086569 | 0.60767 | 0.41692
2025-06-14 21:00 | 34.2723 | 5.6176 | 0.83082 | 0.84859 | 19.6029 | 4.3331 | 12.8395 | 193.3977 | 14.6349 | 194.1207 | 25.8787 | 21.0185 | 13.9398 | 197.8293 | 29.2655 | 20.7368 | 13.7507 | 195.8085 | 19.4342 | 41.13 | 14.0723 | 196.3206 | 20.4213 | 41.1585 | 13.9909 | 197.2409 | 194.9671 | 13.2492 | 43.0734 | 5.335 | 9.9735 | 0 | 81.4186 | 22.505 | 45.1196 | 13.5145 | 191.72 | 194.8667 | 13.1642 | 3.2599 | 50.2735 | 98.2309 | 148.5044 | 9.6199 | 139.7559 | 92.3104 | 12.8899 | 8.2385 | 14.6349 | 194.1207 | 91.7608 | 14.091 | 0.92658 | 0.26199 | 92.8688 | 0.10877 | 0.12799 | 2.7653 | 0.086846 | 0.60412 | 0.41602
2025-06-14 22:00 | 34.5053 | 5.5451 | 0.83319 | 0.85178 | 19.5245 | 4.2802 | 12.8553 | 193.4811 | 14.6465 | 194.0711 | 26.1925 | 20.6719 | 13.9672 | 197.9425 | 29.2989 | 20.7359 | 13.772 | 195.8953 | 19.4288 | 41.0991 | 14.0948 | 196.399 | 20.4374 | 41.1274 | 14.0024 | 197.114 | 195.0696 | 13.2712 | 43.4059 | 5.5622 | 9.972 | 0 | 81.4752 | 22.4973 | 44.7875 | 13.5294 | 191.7908 | 194.9516 | 13.1812 | 3.1413 | 49.8658 | 97.8226 | 147.6884 | 9.5858 | 139.588 | 92.9615 | 12.8898 | 8.211 | 14.6465 | 194.0711 | 91.5594 | 14.0931 | 0.92906 | 0.25862 | 91.9602 | 0.10863 | 0.13071 | 1.7052 | 0.086582 | 0.60848 | 0.41365
2025-06-14 23:00 | 34.539 | 5.5332 | 0.82375 | 0.84297 | 19.2922 | 4.2024 | 12.877 | 193.5694 | 14.6481 | 194.0599 | 26.7824 | 20.1716 | 13.9944 | 198.0646 | 29.3444 | 20.7359 | 13.7898 | 195.9728 | 19.3792 | 40.6023 | 14.0984 | 196.4228 | 20.421 | 40.6316 | 14.0105 | 197.1195 | 195.1763 | 13.2985 | 43.6698 | 5.7914 | 9.9687 | 0 | 81.5185 | 22.491 | 44.0308 | 13.5482 | 191.8706 | 195.048 | 13.2035 | 3.5423 | 49.6273 | 95.52 | 145.1474 | 9.3302 | 138.1913 | 92.6769 | 12.8897 | 7.9842 | 14.6481 | 194.0599 | 90.733 | 14.0808 | 0.93403 | 0.25756 | 91.8523 | 0.10838 | 0.13396 | 0.61621 | 0.08625 | 0.61161 | 0.39348
2025-06-15 | 34.6289 | 4.8278 | 0.81274 | 0.82875 | 18.8628 | 3.6607 | 12.9849 | 194.0645 | 13.6401 | 194.2388 | 28.0414 | 20.0122 | 14.1127 | 198.5773 | 29.3714 | 20.7359 | 13.8959 | 196.335 | 19.3291 | 40.3395 | 14.1842 | 196.721 | 19.747 | 40.3807 | 14.0889 | 197.4606 | 195.7166 | 13.4233 | 44.5408 | 6.0602 | 9.9696 | 0 | 81.5569 | 22.4923 | 41.9964 | 13.6495 | 192.1466 | 195.5237 | 13.314 | 2.9755 | 54.1818 | 72.5839 | 126.7657 | 7.0869 | 122.3429 | 92.0745 | 12.8899 | 6.034 | 13.6401 | 194.2388 | 91.4743 | 13.0245 | 1.8616 | 1.1617 | 90.7325 | 0.85835 | 0.13763 | 0.87212 | 0.86245 | 1.5139 | 1.1135
Total | MW: 814.1613; MVAR: 137.1465; kg/s: 3764673.2295; kg/s: 280280.7473; kg/s: 4202881.3607; kg/s: 6837670.5781; kg/s: 11040551.9387; kg/s: 11352910.8002
Average | 33.9234 | 5.7144 | 0.83771 | 0.85398 | 19.4515 | 3.7677 | 13.089 | 194.2638 | 14.1469 | 194.3964 | 25.3688 | 20.947 | 14.1886 | 198.6051 | 27.8589 | 20.6327 | 14.0066 | 196.7337 | 20.1344 | 38.4754 | 14.2592 | 196.9665 | 20.9816 | 39.1072 | 14.2035 | 197.9434 | 195.8259 | 13.508 | 43.5726 | 4.8779 | 9.9754 | 0 | 80.5192 | 23.2151 | 38.9082 | 13.7455 | 192.3987 | 195.6526 | 13.4034 | 3.244 | 48.6445 | 79.1397 | 127.7842 | 8.6982 | 131.3994 | 91.4391 | 19.8602 | 6.9763 | 14.1469 | 194.3964 | 90.4929 | 13.61 | 0.95337 | 0.2905 | 91.6374 | 0.22063 | 0.12728 | 1.7298 | 0.34189 | 0.79739 | 1.8816
Min | 33.1973 | 3.1427 | 0.77683 | 0.79008 | 17.8848 | 3.018 | 12.6183 | 192.6445 | 13.3771 | 193.3158 | 22.7434 | 15.7452 | 13.6209 | 196.7208 | 26.2406 | 15.9001 | 13.4708 | 194.8621 | 19.2036 | 33.9622 | 13.7958 | 195.8388 | 19.747 | 33.9046 | 13.7192 | 196.3354 | 194.1224 | 12.9995 | 41.1024 | 4.3094 | 9.9687 | 0 | 78.7339 | 22.491 | 32.1635 | 13.3216 | 191.1293 | 194.1061 | 12.9498 | 2.7741 | 45.0942 | 54.7292 | 103.6654 | 7.0869 | 122.3429 | 89.9765 | 12.8897 | 6.034 | 13.3771 | 193.3158 | 88.9204 | 12.8742 | 0.8021 | 0.20738 | 90.6189 | 0.10718 | 0.11298 | 0.068756 | 0.084602 | 0.46492 | 0.39348
Max | 34.6289 | 8.0762 | 0.92987 | 0.95272 | 21.8146 | 4.3957 | 13.6533 | 196.1875 | 14.6784 | 195.8335 | 28.0414 | 24.0852 | 14.7848 | 200.3442 | 29.3714 | 23.8187 | 14.5884 | 198.4174 | 21.2737 | 42.6745 | 14.8981 | 198.8818 | 21.9655 | 45.8207 | 14.8498 | 200.0852 | 197.7654 | 14.0973 | 45.1907 | 6.0602 | 9.9894 | 0 | 81.5569 | 23.8884 | 47.6527 | 14.3114 | 194.1955 | 197.5219 | 13.958 | 3.876 | 54.1818 | 100.6018 | 148.5044 | 10.803 | 139.9452 | 92.9615 | 24.5681 | 8.2385 | 14.6784 | 195.8335 | 92.0743 | 14.3054 | 1.8616 | 1.1617 | 92.8688 | 1.0507 | 0.1461 | 7.0629 | 2.7493 | 1.5462 | 6.4329

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1
18 |  | Night | 22:15 | 5.55 | 22.2
19 | 2025-06-10 | Day | 8:55 | 5.69 | 31.6
20 |  | Night | 0:20 | 5.18 | 24.3
21 | 2025-06-11 | Day | 17:00 | 5.07 | 21.6
22 |  | Night | 22:30 | 5.62 | 28.8
23 | 2025-06-12 | Day | 10:10 | 5.08 | 27.3
24 |  | Night | 21:30 | 5.64 | 26.6
25 | 2025-06-13 | Day | 8:40 | 5.11 | 27.1
26 |  | Night | 22:00 | 5.77 | 25.5
27 | 2025-06-14 | Day | 10:00 | 5.55 | 32
28 |  | Night | 22:00 | 5.78 | 28.9
29 | 2025-06-15 | Day
30 |  | Night
31 | 2025-06-16 | Day
32 |  | Night
33 | 2025-06-17 | Day
34 |  | Night
35 | 2025-06-18 | Day
36 |  | Night
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-14
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0