## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-15
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 26.9411 | 198.1696 | 18.5893
|  | #6-2 | Production | 29.8821 | 196.0951 | 18.7351
|  | #6-3 | Production | 19.4331 | 196.4645 | 41.0775
|  | #6-4 | Production | 20.5019 | 197.6156 | 40.3191
|  | #8-1 | Shut in | 5.8754 | 81.998 | 9.975
|  | #8-2 | Production | 22.2441 | 191.915 | 47.0715
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 44.4639 | 3841679.9314
|  | PAD #8 - STEAM |  |  |  |  | 3.5695 | 308403.4937 | Online
|  | BRINE HEADER |  |  |  |  | 87.8708 | 7592038.9552 | Offline
|  | TOTAL FLOW |  |  |  |  | 135.9042 | 11742122.3803
|  | PRESS SEPARATOR IJN 6 | Online | 13.359 | 195.3366
|  | PRESS SEPARATOR IJN 8 | Online | 13.2518 | 195.1779
| INJECTION WELL | #5-1 | Injection | 6.5397 | 92.7336 | 13.7549 | 131.504 | 11361944.9551
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.3293 |  |  | 823.9025
|  | NET | 0 |  |  | 0
| PARASITIC LOAD |  | 34.3293 |  |  | 823.9025
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 3.9588 |  |  | 14251.8354
|  | NET | 0 |  |  | 0
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-15
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama | [5 empty] | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 760260 | [7 empty] | 760260
M-T-D GROSS GENERATION (kWHR) |  |  |  | 35998565 | [7 empty] | 35998565
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18627.22 | 0 | 3778.21 | 44.5 | 734 | 760 | 23943.93
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 274821.66 | -283254.3 | 80103.59 | 654.8 | 18273 | 21489 | 120520.39
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.3293 |  |  | 4.3562 |  | 18.8361
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 360
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 0%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 3841.6799 |  | 308.4035 |  |  | 4485.9507
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.044464 |  | 0.0035695 |  |  | 0.051921
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 7592.039
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.087871
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 12077.9897
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.13979
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 193.6841 |  |  |  | 194.0347
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.9183 |  |  |  | 14.9364
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 16.8242 |  | 21.1741 |  |  | 18.8361
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [14 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [13 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:01 | PLN adviced load ROH 31.05 MW (Mr. Gedhon Suhendro)
7:45 | Handover night shift to day shift
8:15 | Daily toolbox meeting and safety talk
9:30 | Inspection of Switchgears. Result: Normal and no alarm [Standard Activity]
9:50 | Install strainer brine gathering SP-2501B after cleaning by maintenance
10:05 | P8401 Oil Sump Pump run test for 10 minutes. Discharge pressure 2.8 barg, sump pit level before: 15.7% / after: 15.2% [Standard activity]
10:36 | Switch strainer brine gathering SP-2501A to SP-2501B
10:45 | Drain strainer brine gathering SP-2501A [Standard activity]
11:13 | Changeover GCW pump A to B because found oil leaks on pump bearing. Discharge pressure before: 3.09 barg / after: 3.23 barg
12:00 | Reset MOV IJN 5 because stuck on 12.9%
12:13 | Rectify PT-2702A because found dirty on tube while flushing by maintenance
15:50 | Test run of Pit Pump IJN 6 - Engine (P2203B). Result: Trip on >1100rpm [Standard activity]
16:00 | Test run of Pit Pump IJN 6 - Electric (P2203A) 10 minutes. Discharge pressure 17.5 barg / 95 A [Standard activity]
16:07 | Reinstall PT-2702A after cleaning by maintenance
16:42 | Test run of Pit Pump IJN 8 - Electric (P2303) 10 minutes. Discharge pressure 21.5 barg / 129 A [Standard activity]
18:25 | Ormat (Elad Salomon) remoted HMI by TeamViewer
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Hary |  |  |  | CCR Operator : Fauzan |  |  |  | Steamfield : Vandy
Night Shift | Shift Leader : Arbima |  |  |  | CCR Operator : Dwiki |  |  |  | Steamfield : Rafly
22
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-15
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2192200 | 2213600 | 21400 | 85750
(BACKUP) |  | 2126290 | 2190560 | 2211940 | 21380 | 85650
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 103755450 | 104515710 | 760260 | 11413800
(BACKUP) |  | 93082960 | 103733480 | 104493530 | 760050 | 11410570
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4647420 | 4664550 | 17130 | 522320
(BACKUP) |  | 4144060 | 4649390 | 4666530 | 17140 | 522470
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 112906680 | 137321820 | 24415140 | 35998565
TOTAL |  |  |  |  | 24415140 | 35998565
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 18555179 | 18661152 | 105973 | 2130897
TOTAL |  |  |  |  | 105973 | 2130897
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3345512.78 | 3364140 | 18627.22 | 274821.66
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1066083.79 | 1069862 | 3778.21 | 80103.59
U Ijen 5 |  | 7258.6 | 7868.9 | 7913.4 | 44.5 | 654.8
U Ijen 6 |  | 247889 | 265428 | 266162 | 734 | 18273
U Ijen 8 |  | 299837 | 320566 | 321326 | 760 | 21489
TOTAL |  |  |  |  | 23943.93 | 395342.05
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-15 01:00 | 34.5718 | 3.0996 | 0.80653 | 0.82266 | 18.7122 | 3.8196 | 12.9899 | 193.9622 | 13.9892 | 194.1995 | 27.8948 | 20.0376 | 14.1072 | 198.5009 | 29.4398 | 20.7008 | 13.8988 | 196.3206 | 19.4087 | 39.9043 | 14.1885 | 196.9419 | 20.5399 | 38.6808 | 14.0932 | 197.4475 | 195.6292 | 13.4337 | 44.8189 | 6.1325 | 9.9704 | 0 | 81.609 | 22.5034 | 42.1789 | 13.6554 | 192.2055 | 195.4589 | 13.3187 | 2.743 | 52.5253 | 79.5249 | 132.0502 | 7.4281 | 127.7111 | 91.6926 | 12.8908 | 6.2891 | 13.9892 | 194.1995 | 88.8995 | 13.3424 | 1.1729 | 0.45617 | 91.17 | 0.10718 | 0.1461 | 0.068756 | 0.08474 | 1.5462 | 1.0507
2025-06-15 02:00 | 34.3423 | 1.4135 | 0.80386 | 0.81825 | 18.3436 | 3.432 | 12.9891 | 193.9362 | 13.7019 | 194.0212 | 27.6055 | 20.0431 | 14.0894 | 198.4302 | 29.4982 | 20.2705 | 13.8878 | 196.2679 | 19.562 | 40.2568 | 14.1892 | 196.8967 | 20.468 | 37.8503 | 14.0692 | 197.4523 | 195.5964 | 13.4287 | 44.6981 | 6.1126 | 9.969 | 0 | 81.6741 | 22.5252 | 41.8832 | 13.6553 | 192.2013 | 195.3901 | 13.3167 | 3.0742 | 50.8845 | 66.9784 | 117.8629 | 7.0672 | 126.2301 | 91.6571 | 12.891 | 5.9534 | 13.7019 | 194.0212 | 88.3534 | 13.009 | 1.0879 | 0.36843 | 90.9329 | 0.10727 | 0.14441 | 0.068775 | 0.084709 | 0.90341 | 0.40022
2025-06-15 03:00 | 34.2207 | 0.7776 | 0.81455 | 0.82757 | 17.489 | 3.4597 | 12.8742 | 193.5406 | 13.6476 | 193.6772 | 27.4105 | 20.0509 | 13.9652 | 198.0515 | 29.5482 | 19.8768 | 13.7679 | 195.8568 | 19.4136 | 38.4302 | 14.0414 | 196.4487 | 20.4389 | 39.5655 | 13.9724 | 196.9802 | 195.2032 | 13.3122 | 44.5145 | 6.1318 | 9.9724 | 0 | 81.6617 | 22.5257 | 43.5062 | 13.5543 | 191.8296 | 195.019 | 13.207 | 3.9118 | 51.0085 | 67.3852 | 118.3937 | 6.9745 | 125.9656 | 91.5824 | 12.8906 | 5.8616 | 13.6476 | 193.6772 | 88.0455 | 12.969 | 1.0904 | 0.36531 | 90.9342 | 0.10759 | 0.13721 | 0.068976 | 0.084923 | 0.89918 | 0.39972
2025-06-15 04:00 | 34.3908 | 1.0054 | 0.79875 | 0.81132 | 16.8337 | 3.8541 | 12.8783 | 193.5529 | 13.8804 | 193.7585 | 27.2589 | 20.058 | 13.9568 | 198.04 | 29.5956 | 19.8807 | 13.7636 | 195.8158 | 19.3424 | 37.6166 | 14.021 | 196.2248 | 20.7943 | 40.2786 | 13.9928 | 196.9705 | 195.1933 | 13.3114 | 44.2107 | 6.2562 | 9.976 | 0 | 81.5767 | 22.4741 | 44.232 | 13.5599 | 191.728 | 195.0767 | 13.2126 | 3.8494 | 51.3146 | 81.232 | 132.5467 | 7.1327 | 127.5626 | 91.7017 | 12.8904 | 5.9897 | 13.8804 | 193.7585 | 88.2174 | 13.2129 | 1.0923 | 0.36562 | 91.0757 | 0.10763 | 0.13493 | 0.069014 | 0.084961 | 0.89612 | 0.39851
2025-06-15 05:00 | 34.5328 | 1.6032 | 0.7811 | 0.79043 | 16.8242 | 3.8049 | 13.0119 | 193.965 | 14.067 | 193.9211 | 27.1101 | 19.9889 | 14.0918 | 198.4313 | 29.643 | 19.8079 | 13.9039 | 196.205 | 19.8791 | 39.2588 | 14.1976 | 196.6459 | 20.7284 | 39.3567 | 14.1212 | 197.486 | 195.595 | 13.4444 | 44.2832 | 6.3682 | 9.9728 | 0 | 81.4945 | 22.4298 | 43.2248 | 13.6788 | 191.9962 | 195.4586 | 13.341 | 3.407 | 49.2913 | 82.1038 | 131.3951 | 7.1826 | 128.6217 | 91.9655 | 12.8905 | 6.019 | 14.067 | 193.9211 | 88.4246 | 13.3807 | 1.0879 | 0.36625 | 90.6189 | 0.10724 | 0.14059 | 0.068803 | 0.084602 | 0.89895 | 0.39754
2025-06-15 06:00 | 34.4602 | 2.0607 | 0.79765 | 0.80902 | 17.672 | 3.9281 | 13.0758 | 194.1806 | 14.3796 | 194.2496 | 26.5823 | 19.4196 | 14.1584 | 198.5812 | 29.6882 | 19.6301 | 13.9761 | 196.5193 | 20.1152 | 41.2349 | 14.2997 | 197.0294 | 20.5067 | 39.0275 | 14.1858 | 197.6907 | 195.7806 | 13.5008 | 43.9643 | 6.4332 | 9.9717 | 0 | 81.4638 | 22.4427 | 43.8272 | 13.7395 | 192.2351 | 195.6328 | 13.401 | 3.6203 | 48.7021 | 86.6596 | 135.3617 | 7.6353 | 132.1044 | 91.9595 | 12.891 | 6.4059 | 14.3796 | 194.2496 | 89.0017 | 13.6664 | 1.0766 | 0.36597 | 91.1732 | 0.10768 | 0.14029 | 0.069417 | 0.085688 | 0.89802 | 0.40234
2025-06-15 07:00 | 34.4311 | 2.6836 | 0.82217 | 0.8387 | 19.0015 | 4.0373 | 13.002 | 193.9776 | 14.4184 | 194.3955 | 26.642 | 18.5246 | 14.0972 | 198.4015 | 29.7211 | 19.6427 | 13.9138 | 196.4695 | 19.5685 | 41.9612 | 14.2014 | 196.8026 | 20.5395 | 39.6065 | 14.1464 | 197.7246 | 195.5967 | 13.4334 | 44.0448 | 6.3106 | 9.978 | 0 | 81.6234 | 22.473 | 45.9207 | 13.6862 | 192.2574 | 195.4524 | 13.3305 | 3.4902 | 51.4859 | 87.5225 | 139.0085 | 7.8721 | 133.343 | 92.4391 | 12.893 | 6.6276 | 14.4184 | 194.3955 | 89.3214 | 13.7094 | 1.0464 | 0.3662 | 92.1694 | 0.11092 | 0.12401 | 0.072187 | 0.089343 | 0.86987 | 0.40209
2025-06-15 08:00 | 34.5754 | 3.3589 | 0.84434 | 0.86258 | 19.7111 | 3.9814 | 12.9837 | 193.9549 | 14.3051 | 194.335 | 27.1699 | 18.1262 | 14.1274 | 198.4768 | 29.7615 | 19.7639 | 13.9289 | 196.5192 | 19.3713 | 41.97 | 14.1929 | 196.7915 | 20.7782 | 39.459 | 14.1603 | 197.9584 | 195.6478 | 13.44 | 44.915 | 6.0856 | 9.9782 | 0 | 81.9542 | 22.4986 | 46.1178 | 13.6891 | 192.4051 | 195.445 | 13.3155 | 3.3074 | 54.7292 | 82.9278 | 137.6569 | 7.5393 | 130.7661 | 92.5017 | 12.8966 | 6.3507 | 14.3051 | 194.335 | 88.7411 | 13.5949 | 0.99495 | 0.34913 | 92.7021 | 0.11445 | 0.11464 | 0.075609 | 0.09292 | 1.4454 | 4.2016
2025-06-15 09:00 | 34.5081 | 4.0648 | 0.86768 | 0.88786 | 20.3318 | 3.9873 | 12.9397 | 193.8046 | 14.2558 | 194.2636 | 27.1833 | 18.1222 | 14.1162 | 198.3617 | 29.8197 | 19.5249 | 13.9117 | 196.386 | 19.4916 | 41.9832 | 14.1936 | 196.7564 | 20.7196 | 39.608 | 14.115 | 197.5385 | 195.5262 | 13.4071 | 45.2227 | 5.7078 | 9.979 | 0 | 82.3154 | 22.5075 | 46.1282 | 13.6597 | 192.3389 | 195.2836 | 13.2715 | 3.6963 | 55.5699 | 82.0237 | 137.5936 | 7.3727 | 130.1311 | 92.1032 | 12.9001 | 6.1988 | 14.2558 | 194.2636 | 88.9221 | 13.5354 | 0.95069 | 0.30889 | 91.8482 | 0.11642 | 0.11724 | 0.077579 | 0.094482 | 1.2906 | 6.3753
2025-06-15 10:00 | 34.5226 | 4.9889 | 0.89398 | 0.91282 | 21.0675 | 4.0022 | 12.9006 | 193.6287 | 14.2673 | 194.0705 | 27.1173 | 18.1227 | 14.0895 | 198.2125 | 29.8577 | 18.6519 | 13.8838 | 196.2267 | 19.4416 | 41.9917 | 14.1743 | 196.6107 | 20.7453 | 40.2679 | 14.0822 | 197.1654 | 195.352 | 13.3709 | 45.3355 | 5.3327 | 9.9856 | 0 | 82.6079 | 22.4895 | 46.7844 | 13.6257 | 192.1622 | 195.1011 | 13.2327 | 3.7696 | 54.03 | 84.1368 | 138.1668 | 7.4713 | 131.0838 | 92.3846 | 12.9017 | 6.281 | 14.2673 | 194.0705 | 89.5468 | 13.5399 | 0.94625 | 0.27617 | 91.6116 | 0.11668 | 0.11705 | 0.097517 | 2.7481 | 0.5283 | 4.4328
2025-06-15 11:00 | 34.2697 | 5.3114 | 0.89606 | 0.91086 | 21.1741 | 4.2181 | 12.9194 | 193.6798 | 14.7216 | 194.0455 | 26.438 | 18.1322 | 14.0933 | 198.124 | 29.873 | 18.0191 | 13.8821 | 196.2123 | 19.377 | 41.9968 | 14.1767 | 196.5946 | 20.827 | 40.5421 | 14.1 | 197.581 | 195.3228 | 13.3659 | 44.3365 | 5.2439 | 9.9871 | 0 | 82.781 | 22.4475 | 48.5586 | 13.6577 | 192.1967 | 195.1579 | 13.2533 | 3.5401 | 51.3135 | 93.2388 | 144.5524 | 8.3661 | 135.2974 | 92.7022 | 12.9007 | 6.809 | 14.7216 | 194.0455 | 90.745 | 13.9431 | 0.97287 | 0.27372 | 91.7222 | 0.11761 | 0.11689 | 2.1554 | 2.7493 | 0.49108 | 3.7308
2025-06-15 12:00 | 34.2325 | 5.3553 | 0.8909 | 0.90883 | 20.96 | 4.3054 | 12.9529 | 193.7949 | 15.4496 | 194.308 | 26.5494 | 18.1417 | 14.1132 | 198.2163 | 29.8997 | 18.0139 | 13.9042 | 196.2971 | 19.3188 | 42.002 | 14.1914 | 196.6587 | 20.5385 | 41.0041 | 14.1363 | 197.9846 | 195.42 | 13.393 | 44.1507 | 4.9784 | 9.9843 | 0 | 82.8728 | 22.3309 | 49.6896 | 13.6995 | 192.2904 | 195.2908 | 13.2906 | 3.8508 | 52.036 | 95.3482 | 147.3842 | 5.9344 | 135.5799 | 93.629 | 13.5479 | 6.5887 | 15.4496 | 194.308 | 91.1753 | 14.7593 | 0.99243 | 0.28435 | 91.3015 | 0.11923 | 0.11828 | 2.138 | 0.094018 | 0.46492 | 3.5731
2025-06-15 13:00 | 34.5837 | 5.5481 | 0.89531 | 0.91783 | 20.8323 | 4.1551 | 13.0351 | 194.0776 | 15.5356 | 194.3853 | 27.2505 | 18.1398 | 14.2203 | 198.6048 | 29.9509 | 18.0163 | 14.0085 | 196.6255 | 19.3415 | 42.0013 | 14.2847 | 196.9222 | 20.5208 | 41.1028 | 14.2369 | 198.3069 | 195.762 | 13.4975 | 45.0779 | 4.7971 | 9.985 | 0 | 82.9622 | 22.2043 | 49.375 | 13.7737 | 192.4682 | 195.5833 | 13.3737 | 3.5441 | 54.3978 | 89.3016 | 143.6993 | 1.3044 | 131.6253 | 93.3836 | 14.3918 | 6.3384 | 15.5356 | 194.3853 | 89.8704 | 14.9585 | 0.98237 | 0.28354 | 91.6415 | 0.1184 | 0.11714 | 0.079219 | 0.093278 | 0.48636 | 5.2499
2025-06-15 14:00 | 34.4488 | 5.5779 | 0.88347 | 0.91215 | 20.1974 | 4.2782 | 12.9579 | 193.8006 | 15.9394 | 194.1613 | 26.495 | 18.137 | 14.1389 | 198.2796 | 29.9857 | 18.0133 | 13.9293 | 196.3247 | 19.3918 | 42.0013 | 14.2378 | 196.7135 | 20.5814 | 41.8058 | 14.1757 | 198.1437 | 195.453 | 13.4075 | 44.6335 | 4.9827 | 9.9822 | 0 | 82.9866 | 22.1177 | 50.0664 | 13.6868 | 192.1681 | 195.3116 | 13.294 | 3.3903 | 53.0525 | 94.3279 | 147.3804 | 0.0012028 | 134.2369 | 92.3831 | 14.5848 | 7.1054 | 15.9394 | 194.1613 | 89.4909 | 15.359 | 0.99094 | 0.27524 | 91.2549 | 0.11503 | 0.11407 | 0.07656 | 0.091302 | 0.53067 | 6.4329
2025-06-15 15:00 | 34.237 | 5.4071 | 0.89479 | 0.92854 | 19.5553 | 4.2691 | 12.8489 | 193.4467 | 15.7926 | 194.0275 | 26.5124 | 18.1244 | 13.9899 | 197.9353 | 29.9933 | 17.995 | 13.7952 | 195.8913 | 19.3114 | 41.5499 | 14.1228 | 196.3021 | 20.4325 | 41.7153 | 14.0504 | 197.8269 | 195.1049 | 13.2902 | 44.596 | 5.2052 | 9.9744 | 0 | 82.8083 | 22.0295 | 49.6821 | 13.558 | 191.7709 | 194.9714 | 13.1869 | 3.9062 | 52.1289 | 94.0331 | 146.162 | 5.6e-06 | 133.3284 | 93.0624 | 14.5795 | 7.0758 | 15.7926 | 194.0275 | 89.2779 | 15.2284 | 1.0268 | 0.28796 | 90.7488 | 0.11069 | 0.11298 | 4.267 | 0.088346 | 0.58167 | 3.2965
2025-06-15 16:00 | 34.1505 | 5.0769 | 0.9248 | 0.95237 | 19.4815 | 4.1366 | 12.7937 | 193.2787 | 15.0433 | 193.8852 | 27.2232 | 18.1089 | 13.9107 | 197.856 | 30.0138 | 17.9817 | 13.7255 | 195.7028 | 19.2355 | 41.0534 | 14.0396 | 196.0029 | 20.2805 | 40.9337 | 13.9717 | 197.6021 | 194.9705 | 13.2411 | 45.1412 | 5.3512 | 9.9715 | 0 | 82.5643 | 21.9832 | 49.4207 | 13.4944 | 191.5106 | 194.7964 | 13.1359 | 3.9074 | 52.3988 | 88.8696 | 141.2684 | 5.2934 | 129.7793 | 93.3441 | 14.5763 | 6.1219 | 15.0433 | 193.8852 | 88.9348 | 14.4832 | 1.039 | 0.3036 | 91.2843 | 0.85227 | 0.11575 | 7.0629 | 0.086722 | 0.60951 | 0.41624
2025-06-15 17:00 | 33.8294 | 6.5568 | 0.91794 | 0.93643 | 19.189 | 4.3426 | 12.7098 | 192.982 | 15.8054 | 193.6357 | 26.4399 | 18.1072 | 13.8078 | 197.4809 | 30.0377 | 17.9809 | 13.6285 | 195.4031 | 19.3665 | 41.0125 | 13.9512 | 195.7321 | 20.2587 | 41.0232 | 13.8791 | 197.2515 | 194.6171 | 13.1376 | 44.2563 | 5.4624 | 9.9682 | 0 | 82.3389 | 21.9702 | 49.9246 | 13.4107 | 191.1756 | 194.4883 | 13.0494 | 3.8029 | 51.6935 | 95.2127 | 146.9061 | 12.085 | 133.845 | 93.0994 | 14.5759 | 6.5177 | 15.8054 | 193.6357 | 89.592 | 15.2198 | 1.0377 | 0.30152 | 92.3537 | 1.0507 | 0.12334 | 4.5378 | 0.086395 | 0.61722 | 0.41463
2025-06-15 18:00 | 33.978 | 7.8604 | 0.90361 | 0.91961 | 18.5923 | 4.3411 | 12.7949 | 193.2475 | 15.9432 | 193.7323 | 26.5209 | 18.1071 | 13.8899 | 197.72 | 30.0558 | 17.9814 | 13.7104 | 195.6363 | 19.4045 | 41.0139 | 14.0293 | 195.9419 | 20.3663 | 41.0157 | 13.9619 | 197.5028 | 194.8783 | 13.2225 | 44.1601 | 5.652 | 9.9659 | 0 | 82.1031 | 21.9579 | 49.3688 | 13.4872 | 191.3486 | 194.749 | 13.1312 | 3.9012 | 51.7733 | 95.729 | 147.5023 | 12.8869 | 134.0841 | 94.0222 | 14.5757 | 7.2109 | 15.9432 | 193.7323 | 89.6032 | 15.3318 | 1.0396 | 0.29821 | 92.7539 | 0.30673 | 0.12928 | 5.365 | 0.086314 | 0.61969 | 0.41465
2025-06-15 19:00 | 34.0449 | 7.5273 | 0.89933 | 0.91454 | 18.214 | 4.2294 | 12.7994 | 193.2942 | 15.3269 | 193.9011 | 26.7523 | 18.1061 | 13.8965 | 197.8067 | 30.0758 | 17.9815 | 13.7176 | 195.6941 | 19.2746 | 41.0136 | 14.0276 | 195.9474 | 20.3359 | 41.0164 | 13.9692 | 197.5724 | 194.9557 | 13.2356 | 44.5879 | 5.8401 | 9.9667 | 0 | 81.8926 | 21.9578 | 49.2564 | 13.4917 | 191.4329 | 194.8012 | 13.1364 | 3.9731 | 52.7036 | 91.2845 | 143.9881 | 12.2322 | 131.0808 | 93.7388 | 14.5752 | 6.8084 | 15.3269 | 193.9011 | 88.9409 | 14.7035 | 1.0393 | 0.29934 | 92.0986 | 0.10849 | 0.13076 | 5.6233 | 0.086369 | 0.6144 | 0.41571
2025-06-15 20:00 | 34.0843 | 7.3869 | 0.85899 | 0.86951 | 17.9364 | 4.3021 | 12.8375 | 193.3994 | 15.7426 | 193.82 | 26.5469 | 18.1076 | 13.9265 | 197.8335 | 30.098 | 17.9821 | 13.7453 | 195.7268 | 19.4114 | 41.0121 | 14.0586 | 196.0458 | 20.3568 | 40.7199 | 13.9917 | 197.608 | 195.0193 | 13.2624 | 43.8726 | 6.0174 | 9.9699 | 0 | 81.6944 | 21.9712 | 48.7903 | 13.525 | 191.4641 | 194.9112 | 13.171 | 3.6396 | 51.6436 | 94.9893 | 146.6329 | 12.5698 | 133.1399 | 93.3781 | 14.575 | 6.9883 | 15.7426 | 193.82 | 89.2337 | 15.1006 | 1.0404 | 0.29443 | 92.4883 | 0.10872 | 0.12951 | 3.5147 | 0.086569 | 0.60767 | 0.41692
2025-06-15 21:00 | 34.3184 | 6.0237 | 0.82959 | 0.83543 | 17.6086 | 4.2007 | 12.905 | 193.6428 | 15.5364 | 193.8533 | 27.1542 | 18.1095 | 14.0076 | 198.109 | 30.1258 | 17.9834 | 13.8194 | 195.9342 | 19.4104 | 41.0835 | 14.1249 | 196.2039 | 20.3289 | 40.4879 | 14.0537 | 197.6956 | 195.2815 | 13.3384 | 44.1129 | 6.2766 | 9.9736 | 0 | 81.4913 | 21.9807 | 47.9683 | 13.5894 | 191.6316 | 195.1727 | 13.2387 | 3.29 | 51.045 | 93.1152 | 144.1602 | 12.2986 | 132.0095 | 93.2218 | 14.575 | 6.8592 | 15.5364 | 193.8533 | 88.7499 | 14.869 | 1.0481 | 0.29138 | 92.8688 | 0.10877 | 0.12799 | 2.7653 | 0.086846 | 0.60412 | 0.41602
2025-06-15 22:00 | 34.257 | 4.5843 | 0.83691 | 0.84485 | 17.5119 | 4.3006 | 12.8645 | 193.5044 | 15.746 | 193.8319 | 26.6078 | 18.1098 | 13.9648 | 197.965 | 30.1491 | 17.9831 | 13.7863 | 195.8285 | 19.3589 | 41.5644 | 14.1009 | 196.1026 | 20.4162 | 40.9895 | 14.036 | 197.5679 | 195.1446 | 13.2973 | 44.0652 | 6.5554 | 9.9739 | 0 | 81.3 | 21.9947 | 48.324 | 13.5505 | 191.5168 | 195.0292 | 13.1984 | 3.3449 | 51.5277 | 95.7976 | 147.3253 | 12.4662 | 133.8279 | 92.5612 | 14.5747 | 6.9538 | 15.746 | 193.8319 | 88.6202 | 15.06 | 1.0525 | 0.29562 | 91.9602 | 0.10863 | 0.13071 | 1.7052 | 0.086582 | 0.60848 | 0.41365
2025-06-15 23:00 | 34.4144 | 3.8911 | 0.8124 | 0.82473 | 17.3074 | 4.2427 | 12.9516 | 193.8049 | 15.7873 | 194.1329 | 26.6592 | 18.1101 | 14.041 | 198.1942 | 30.1613 | 17.9807 | 13.8629 | 196.0882 | 19.3917 | 41.9742 | 14.1815 | 196.3571 | 20.35 | 40.6152 | 14.1051 | 197.8157 | 195.4173 | 13.3789 | 43.8164 | 6.8363 | 9.9727 | 0 | 81.1457 | 22.0073 | 47.9276 | 13.629 | 191.7557 | 195.2716 | 13.2821 | 3.6758 | 50.3817 | 95.6288 | 146.0105 | 12.4073 | 133.6608 | 93.4233 | 14.5749 | 6.9773 | 15.7873 | 194.1329 | 88.7991 | 15.0949 | 1.0489 | 0.29871 | 91.8523 | 0.10838 | 0.13396 | 0.61621 | 0.08625 | 0.61161 | 0.39348
2025-06-16 | 34.4982 | 3.3857 | 0.83909 | 0.84451 | 17.5192 | 4.1158 | 13.0224 | 193.9607 | 15.1906 | 194.2213 | 27.4614 | 18.1087 | 14.126 | 198.4576 | 30.1788 | 17.9799 | 13.9423 | 196.3297 | 19.2065 | 41.9745 | 14.2459 | 196.4745 | 20.1921 | 40.9848 | 14.1804 | 197.9021 | 195.6101 | 13.4641 | 44.3186 | 6.939 | 9.9709 | 0 | 81.0301 | 22.0369 | 47.5597 | 13.6981 | 191.8696 | 195.4177 | 13.3533 | 3.0322 | 50.46 | 91.5289 | 141.9889 | 11.8424 | 131.081 | 93.6704 | 14.5745 | 6.6207 | 15.1906 | 194.2213 | 88.8237 | 14.4896 | 1.041 | 0.29782 | 90.7325 | 0.85835 | 0.13763 | 0.87212 | 0.86245 | 1.5139 | 1.1135
Total | MW: 823.9025; MVAR: 104.5492; kg/s: 3841679.9314; kg/s: 308403.4937; kg/s: 4485950.7246; kg/s: 7592038.9552; kg/s: 12077989.6797; kg/s: 11361944.9551
Average | 34.3293 | 4.3562 | 0.85474 | 0.87089 | 18.8361 | 4.0727 | 12.9183 | 193.6841 | 14.9364 | 194.0347 | 26.9411 | 18.5893 | 14.0386 | 198.1696 | 29.8821 | 18.7351 | 13.8456 | 196.0951 | 19.4331 | 41.0775 | 14.1447 | 196.4645 | 20.5019 | 40.3191 | 14.0744 | 197.6156 | 195.3366 | 13.359 | 44.4639 | 5.8754 | 9.975 | 0 | 81.998 | 22.2441 | 47.0715 | 13.6148 | 191.915 | 195.1779 | 13.2518 | 3.5695 | 51.9207 | 87.8708 | 139.7915 | 8.0568 | 131.504 | 92.7336 | 13.7549 | 6.5397 | 14.9364 | 194.0347 | 89.1388 | 14.2734 | 1.0374 | 0.31973 | 91.6374 | 0.22063 | 0.12728 | 1.7298 | 0.34189 | 0.79739 | 1.8816
Min | 33.8294 | 0.7776 | 0.7811 | 0.79043 | 16.8242 | 3.432 | 12.7098 | 192.982 | 13.6476 | 193.6357 | 26.438 | 18.1061 | 13.8078 | 197.4809 | 29.4398 | 17.9799 | 13.6285 | 195.4031 | 19.2065 | 37.6166 | 13.9512 | 195.7321 | 20.1921 | 37.8503 | 13.8791 | 196.9705 | 194.6171 | 13.1376 | 43.8164 | 4.7971 | 9.9659 | 0 | 81.0301 | 21.9578 | 41.8832 | 13.4107 | 191.1756 | 194.4883 | 13.0494 | 2.743 | 48.7021 | 66.9784 | 117.8629 | 5.6e-06 | 125.9656 | 91.5824 | 12.8904 | 5.8616 | 13.6476 | 193.6357 | 88.0455 | 12.969 | 0.94625 | 0.27372 | 90.6189 | 0.10718 | 0.11298 | 0.068756 | 0.084602 | 0.46492 | 0.39348
Max | 34.5837 | 7.8604 | 0.9248 | 0.95237 | 21.1741 | 4.3426 | 13.0758 | 194.1806 | 15.9432 | 194.3955 | 27.8948 | 20.058 | 14.2203 | 198.6048 | 30.1788 | 20.7008 | 14.0085 | 196.6255 | 20.1152 | 42.002 | 14.2997 | 197.0294 | 20.827 | 41.8058 | 14.2369 | 198.3069 | 195.7806 | 13.5008 | 45.3355 | 6.939 | 9.9871 | 0 | 82.9866 | 22.5257 | 50.0664 | 13.7737 | 192.4682 | 195.6328 | 13.401 | 3.9731 | 55.5699 | 95.7976 | 147.5023 | 12.8869 | 135.5799 | 94.0222 | 14.5848 | 7.2109 | 15.9432 | 194.3955 | 91.1753 | 15.359 | 1.1729 | 0.45617 | 92.8688 | 1.0507 | 0.1461 | 7.0629 | 2.7493 | 1.5462 | 6.4329

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1 | 2025-06-09 | 2025-06-09 19:30
18 |  | Night | 22:15 | 5.55 | 22.2 | 2025-06-09 | 2025-06-09 22:15
19 | 2025-06-10 | Day | 8:55 | 5.69 | 31.6 | 2025-06-10 | 2025-06-10 08:55
20 |  | Night | 0:20 | 5.18 | 24.3 | 2025-06-10 | 2025-06-10 00:20
21 | 2025-06-11 | Day | 17:00 | 5.07 | 21.6 | 2025-06-11 | 2025-06-11 17:00
22 |  | Night | 22:30 | 5.62 | 28.8 | 2025-06-11 | 2025-06-11 22:30
23 | 2025-06-12 | Day | 10:10 | 5.08 | 27.3 | 2025-06-12 | 2025-06-12 10:10
24 |  | Night | 21:30 | 5.64 | 26.6 | 2025-06-12 | 2025-06-12 21:30
25 | 2025-06-13 | Day | 8:40 | 5.11 | 27.1 | 2025-06-13 | 2025-06-13 08:40
26 |  | Night | 22:00 | 5.77 | 25.5 | 2025-06-13 | 2025-06-13 22:00
27 | 2025-06-14 | Day | 10:00 | 5.55 | 32 | 2025-06-14 | 2025-06-14 10:00
28 |  | Night | 22:00 | 5.78 | 28.9 | 2025-06-14 | 2025-06-14 22:00
29 | 2025-06-15 | Day | 10:00 | 5.33 | 24.6 | 2025-06-15 | 2025-06-15 10:00
30 |  | Night | 23:45 | 5.82 | 30.3
31 | 2025-06-16 | Day
32 |  | Night
33 | 2025-06-17 | Day
34 |  | Night
35 | 2025-06-18 | Day
36 |  | Night
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-15
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0