## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-16
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 27.479 | 197.8131 | 16.7363
|  | #6-2 | Production | 30.1309 | 195.7205 | 18.2747
|  | #6-3 | Production | 19.2056 | 196.0339 | 41.9923
|  | #6-4 | Production | 19.8221 | 197.6269 | 43.4698
|  | #8-1 | Shut in | 6.4621 | 79.825 | 9.9724
|  | #8-2 | Production | 22.0019 | 191.4149 | 49.6434
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 44.4677 | 3842009.412
|  | PAD #8 - STEAM |  |  |  |  | 3.8724 | 334578.116 | Online
|  | BRINE HEADER |  |  |  |  | 95.2165 | 8226705.5879 | Offline
|  | TOTAL FLOW |  |  |  |  | 143.5566 | 12403293.116
|  | PRESS SEPARATOR IJN 6 | Online | 13.2691 | 195.0277
|  | PRESS SEPARATOR IJN 8 | Online | 13.1649 | 194.8715
| INJECTION WELL | #5-1 | Injection | 7.1547 | 94.7524 | 14.5773 | 134.4753 | 11618661.9132
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.0239 |  |  | 816.5732
|  | NET | 31.3333 |  |  | 752
| PARASITIC LOAD |  | 2.6905 |  |  | 64.5731
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 4.2193 |  |  | 15189.4443
|  | NET | 4.5816 |  |  | 16493.7398
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-16
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 752000.0488 |  | 0 |  | 752000.0488
|  |  |  | 752000.0488 |  | 0 |  | 752000.0488
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 752610 | [7 empty] | 752610
M-T-D GROSS GENERATION (kWHR) |  |  |  | 44177925 | [7 empty] | 44177925
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18619 | 0 | 4285 | 42.6 | 814 | 790 | 24550.6
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 293440.66 | -283254.3 | 84388.59 | 697.4 | 19087 | 22279 | 126451.99
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.0239 |  |  | 5.1078 |  | 19.4132
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 384
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 90.83%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 3842.0094 |  | 334.5781 |  |  | 4429.8773
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.044468 |  | 0.0038724 |  |  | 0.051272
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 8226.7056
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.095216
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 12656.5829
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.14649
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 193.3751 |  |  |  | 193.8593
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.8296 |  |  |  | 16.1594
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 17.5411 |  | 21.5263 |  |  | 19.4132
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [14 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [13 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Power Meter OEC U3B error and record U3B was freeze at hmi oneline
6. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
7. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
8. Brine Dump Control valve Ijen-6 PV-2227A indication passing
9. Compressor A have indication noise on bearing screw pump
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
4:05 | Changover condensate pump-B to A
7:00 | PLN advised ROH at 31.05 MW (Mr. Inggih)
7:07 | Changeover Reinjection Pump-A to B due to cleaning strainer
7:09 | Turn to off the breaker of Reinjection Pump-A and switch to manual the VFD
7:11 | Close manual valve suction and discharge of reinjection pump-A
7:13 | Open drain suction strainer reinjection pump-A
7:45 | Handover night shift to day shift
8:00 | Close discharge valve Reinjection pump A and drain, prepare cleaning strainer A
8:15 | Daily toolbox meeting and safety moment
9:20 | P8051 Backwash Pump of well water treatment system run test [Standard Activity]
10:10 | Flushing water line from WDS to Service Water Tank
10:25 | Check on diesel pit pump 6 by maintenance, troubleshoot trip on >1100rpm
10:30 | Master valve PW IJN 6-1, 6-2, 6-3, 6-4 exercise 10 rotation. Result: all good and normal condition [Standard Activity]
10:45 | Check & Drain Condensate Drain Pot (CDP)&Steam Trap Steam Line IJN 6 Separator Area
10:50 | Draining of Air Vessel Tank on IJN 6 [Standard activity]
10:55 | Drain Suction Strainer Booster Pump A IJN 6 [Standard Activity]
10:58 | Flushing water line from WDS to Service Water Tank done. Top up level SWT from WDS. Level before: 37.4% / after: 42.7%
11:15 | Check & Drain Condensate Drain Pot (CDP)&Steam Trap Steam Line IJN 8 Separator Area [Standard Activity]
11:18 | Check & Drain Condensate Drain Pot (CDP)&Steam Trap Steam Line IJN 8 Near Instrument Air Receiver [Standard Activity]
11:22 | Draining of Air Vessel Tank on IJN 8 [Standard activity]
11:25 | Drain Suction Strainer Booster Pump A IJN 8 [Standard Activity]
11:29 | Check & Drain Condensate Drain Pot (CDP)&Steam Trap Steam Line IJN 6 Near Power Block [Standard activity]
14:19 | Pull out strainer Re injection pump A to cleaning by maintenance
16:00 | Run test diesel pit pump 6 after setting by maintenance. Result: Normal running on 1500 rpm, but found leaks on mechseal
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Hary |  |  |  | CCR Operator : Fauzan |  |  |  | Steamfield : Vandy
Night Shift | Shift Leader : Arbima |  |  |  | CCR Operator : Dwiki |  |  |  | Steamfield : Rafly
22
Note on H13: Operator MPGS: -Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze

## Meter
DATE: | 2025-06-16
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2213600 | 2226060 | 12460 | 98210
(BACKUP) |  | 2126290 | 2211940 | 2224390 | 12450 | 98100
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 104515710 | 105268320 | 752610 | 12166410
(BACKUP) |  | 93082960 | 104493530 | 105245920 | 752390 | 12162960
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4664550 | 4690720 | 26170 | 548490
(BACKUP) |  | 4144060 | 4666530 | 4692710 | 26180 | 548650
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 137321820 | 145501180 | 8179360 | 44177925
TOTAL |  |  |  |  | 8179360 | 44177925
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 18661152 | 18784768 | 123616 | 2254513
TOTAL |  |  |  |  | 123616 | 2254513
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3364140 | 3382759 | 18619 | 293440.66
U3B |  | 283254.3 |  |  | 0 | -283254.3
U3C |  | 989758.41 | 1069862 | 1074147 | 4285 | 84388.59
U Ijen 5 |  | 7258.6 | 7913.4 | 7956 | 42.6 | 697.4
U Ijen 6 |  | 247889 | 266162 | 266976 | 814 | 19087
U Ijen 8 |  | 299837 | 321326 | 322116 | 790 | 22279
TOTAL |  |  |  |  | 24550.6 | 419892.65
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April
Note on G43: Operator MPGS: - Power Meter Error since beginning (construction phase) - Record from HMI oneline was Freeze since 13 April

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-16 01:00 | 34.1568 | 2.6315 | 0.86055 | 0.87047 | 17.5856 | 4.3456 | 12.894 | 193.6195 | 15.958 | 193.873 | 26.793 | 17.4582 | 13.9846 | 198.0217 | 30.1912 | 17.4351 | 13.8159 | 195.9903 | 19.2513 | 41.9746 | 14.1328 | 196.2446 | 20.4109 | 41.6991 | 14.0798 | 197.7908 | 195.2367 | 13.3254 | 43.9708 | 7.1893 | 9.9709 | 0 | 80.9497 | 22.0404 | 48.3356 | 13.5769 | 191.6165 | 195.1262 | 13.2268 | 3.6528 | 51.7792 | 96.6541 | 148.4333 | 12.5466 | 134.6135 | 93.7888 | 14.5746 | 7.0432 | 15.958 | 193.873 | 89.4163 | 15.2391 | 1.0393 | 0.2991 | 91.17 | 0.10718 | 0.1461 | 0.068756 | 0.08474 | 1.5462 | 1.0507
2025-06-16 02:00 | 34.2854 | 2.8821 | 0.88792 | 0.90813 | 18.2713 | 4.3017 | 12.8644 | 193.5143 | 15.8334 | 193.7703 | 27.6795 | 16.5348 | 13.9641 | 197.9713 | 30.2024 | 17.1967 | 13.7951 | 195.8714 | 19.2775 | 41.9743 | 14.1122 | 196.1692 | 20.3653 | 41.8693 | 14.0601 | 197.8042 | 195.1687 | 13.3044 | 44.6506 | 7.3301 | 9.9697 | 0 | 80.836 | 22.0376 | 49.0713 | 13.5514 | 191.4962 | 195.0112 | 13.2001 | 4.181 | 52.6331 | 94.8507 | 147.4839 | 12.4885 | 133.9397 | 94.4052 | 14.575 | 7.0564 | 15.8334 | 193.7703 | 89.748 | 15.1123 | 1.0333 | 0.30229 | 90.9329 | 0.10727 | 0.14441 | 0.068775 | 0.084709 | 0.90341 | 0.40022
2025-06-16 03:00 | 33.9564 | 3.162 | 0.90562 | 0.93251 | 18.9943 | 4.3223 | 12.7912 | 193.237 | 15.7159 | 193.7649 | 27.1485 | 16.1003 | 13.8773 | 197.6575 | 30.198 | 17.0004 | 13.7162 | 195.5555 | 19.2072 | 41.9731 | 14.033 | 195.922 | 20.2297 | 42.4127 | 13.9856 | 197.4957 | 194.881 | 13.2247 | 44.3553 | 7.3307 | 9.9663 | 0 | 80.6768 | 22.0346 | 49.4509 | 13.4843 | 191.2576 | 194.7301 | 13.1274 | 3.9534 | 51.803 | 94.9672 | 146.7702 | 12.352 | 133.4601 | 94.2184 | 14.5753 | 6.9482 | 15.7159 | 193.7649 | 89.6591 | 14.9831 | 1.0274 | 0.29862 | 90.9342 | 0.10759 | 0.13721 | 0.068976 | 0.084923 | 0.89918 | 0.39972
2025-06-16 04:00 | 34.0267 | 2.8617 | 0.89896 | 0.93094 | 19.088 | 4.3645 | 12.8054 | 193.2785 | 16.0216 | 193.8084 | 27.1034 | 16.0988 | 13.9001 | 197.702 | 30.1913 | 16.9997 | 13.7349 | 195.5648 | 19.2214 | 41.9957 | 14.0534 | 195.979 | 20.2031 | 42.8969 | 14.0119 | 197.6082 | 194.927 | 13.2399 | 44.3735 | 7.3 | 9.9641 | 0 | 80.5017 | 22.0224 | 49.2679 | 13.497 | 191.2921 | 194.7831 | 13.1406 | 3.9491 | 51.6861 | 96.822 | 148.5081 | 12.6835 | 134.818 | 94.581 | 14.5753 | 7.186 | 16.0216 | 193.8084 | 89.7517 | 15.2762 | 1.0294 | 0.29488 | 91.0757 | 0.10763 | 0.13493 | 0.069014 | 0.084961 | 0.89612 | 0.39851
2025-06-16 05:00 | 34.1639 | 3.5957 | 0.88486 | 0.92087 | 18.9345 | 4.2374 | 12.8238 | 193.4032 | 15.7976 | 193.9069 | 27.5523 | 16.1005 | 13.9258 | 197.8739 | 30.1993 | 16.524 | 13.7584 | 195.6394 | 19.2013 | 42.0261 | 14.0739 | 196.045 | 20.0313 | 42.8366 | 14.0314 | 197.781 | 195.0877 | 13.2693 | 44.8126 | 7.1989 | 9.9664 | 0 | 80.3029 | 22.0143 | 49.2969 | 13.5176 | 191.4299 | 194.9272 | 13.1619 | 3.9903 | 51.9676 | 92.7973 | 144.7649 | 12.2537 | 132.584 | 94.3449 | 14.5753 | 6.934 | 15.7976 | 193.9069 | 88.8997 | 15.0467 | 1.0341 | 0.29606 | 90.6189 | 0.10724 | 0.14059 | 0.068803 | 0.084602 | 0.89895 | 0.39754
2025-06-16 06:00 | 33.9706 | 3.7819 | 0.86275 | 0.90143 | 18.6744 | 4.3127 | 12.7619 | 193.1829 | 16.213 | 193.7387 | 27.1767 | 16.1025 | 13.8505 | 197.5845 | 30.2075 | 16.0215 | 13.6852 | 195.3646 | 19.2041 | 41.9988 | 14.0027 | 195.7524 | 19.8791 | 42.8742 | 13.9541 | 197.4057 | 194.8244 | 13.1937 | 44.1854 | 7.0186 | 9.9699 | 0 | 80.0946 | 22.0044 | 50.003 | 13.4591 | 191.223 | 194.6976 | 13.0998 | 3.84 | 50.8364 | 95.6684 | 146.5048 | 12.4696 | 134.1018 | 93.6192 | 14.5755 | 7.011 | 16.213 | 193.7387 | 88.9386 | 15.4524 | 1.0373 | 0.29698 | 91.1732 | 0.10768 | 0.14029 | 0.069417 | 0.085688 | 0.89802 | 0.40234
2025-06-16 07:00 | 34.0607 | 2.7896 | 0.87953 | 0.91668 | 18.7961 | 4.3145 | 12.783 | 193.2356 | 16.0695 | 193.7202 | 27.7133 | 16.0975 | 13.8864 | 197.6802 | 30.2189 | 15.9924 | 13.7136 | 195.4411 | 19.1933 | 41.9671 | 14.026 | 195.7198 | 19.8759 | 42.9623 | 13.9774 | 197.3675 | 194.8908 | 13.22 | 44.4974 | 6.9185 | 9.9717 | 0 | 79.9035 | 21.9867 | 50.2138 | 13.4817 | 191.2428 | 194.7473 | 13.1218 | 3.9473 | 51.7964 | 95.1585 | 146.9549 | 12.4449 | 133.9021 | 93.8359 | 14.5758 | 7.0202 | 16.0695 | 193.7202 | 89.0703 | 15.2636 | 1.0298 | 0.30298 | 92.1694 | 0.11092 | 0.12401 | 0.072187 | 0.089343 | 0.86987 | 0.40209
2025-06-16 08:00 | 33.8202 | 3.7286 | 0.90019 | 0.93367 | 19.1459 | 4.3371 | 12.7442 | 193.1229 | 15.8965 | 193.6876 | 27.2577 | 16.7053 | 13.8404 | 197.5359 | 30.2317 | 16.6259 | 13.6695 | 195.3483 | 19.1579 | 41.9732 | 13.9781 | 195.6136 | 19.8771 | 43.0195 | 13.9365 | 197.2696 | 194.7663 | 13.1773 | 44.3136 | 6.8533 | 9.9739 | 0 | 79.764 | 21.9835 | 50.5771 | 13.4489 | 191.1833 | 194.6286 | 13.0825 | 3.9017 | 51.7175 | 94.963 | 146.6805 | 12.4562 | 133.6029 | 93.9656 | 14.5766 | 7.0107 | 15.8965 | 193.6876 | 89.4052 | 15.0582 | 1.0072 | 0.30389 | 92.7021 | 0.11445 | 0.11464 | 0.075609 | 0.09292 | 1.4454 | 4.2016
2025-06-16 09:00 | 33.9023 | 5.8735 | 0.90357 | 0.94266 | 19.5042 | 4.3738 | 12.7401 | 193.0979 | 16.1018 | 193.7156 | 27.2943 | 17.6653 | 13.849 | 197.5152 | 30.2456 | 17.6316 | 13.6718 | 195.358 | 19.2093 | 41.978 | 13.974 | 195.6643 | 19.8836 | 43.0425 | 13.9393 | 197.3154 | 194.7411 | 13.1755 | 44.1428 | 6.8129 | 9.978 | 0 | 79.6944 | 21.9888 | 50.5724 | 13.4515 | 191.1729 | 194.5956 | 13.0777 | 3.8853 | 52.3713 | 95.9105 | 148.2818 | 12.8041 | 134.5218 | 94.87 | 14.5779 | 7.2544 | 16.1018 | 193.7156 | 90.1883 | 15.2618 | 0.96728 | 0.28841 | 91.8482 | 0.11642 | 0.11724 | 0.077579 | 0.094482 | 1.2906 | 6.3753
2025-06-16 10:00 | 33.9212 | 7.126 | 0.89417 | 0.94223 | 19.7764 | 4.3191 | 12.7427 | 193.1023 | 15.9169 | 193.7531 | 27.493 | 18.1477 | 13.8712 | 197.5332 | 30.2706 | 18.1106 | 13.6855 | 195.4034 | 19.1918 | 41.9755 | 13.9738 | 195.7251 | 19.8318 | 43.0404 | 13.9423 | 197.3564 | 194.7581 | 13.1836 | 44.2649 | 6.8389 | 9.9785 | 0 | 79.7135 | 22.0036 | 50.4234 | 13.4638 | 191.2372 | 194.599 | 13.0798 | 3.9453 | 51.7167 | 94.7931 | 146.5098 | 12.6804 | 133.9376 | 95.0233 | 14.5793 | 7.1823 | 15.9169 | 193.7531 | 90.1737 | 15.0721 | 0.92565 | 0.2664 | 91.6116 | 0.11668 | 0.11705 | 0.097517 | 2.7481 | 0.5283 | 4.4328
2025-06-16 11:00 | 33.7696 | 6.8417 | 0.89716 | 0.94987 | 20.3184 | 4.3859 | 12.7114 | 192.9802 | 16.1399 | 193.7008 | 27.3651 | 18.6911 | 13.8479 | 197.4099 | 30.2883 | 18.5571 | 13.6592 | 195.3155 | 19.1942 | 41.9736 | 13.9429 | 195.6884 | 19.806 | 43.0214 | 13.9106 | 197.2459 | 194.6241 | 13.1499 | 44.2573 | 6.847 | 9.9773 | 0 | 79.768 | 22.0087 | 50.5569 | 13.4375 | 191.1979 | 194.4761 | 13.0477 | 3.8643 | 51.6258 | 96.485 | 148.1108 | 12.8503 | 135.0224 | 94.6784 | 14.5805 | 7.2612 | 16.1399 | 193.7008 | 90.3679 | 15.2894 | 0.90943 | 0.26026 | 91.7222 | 0.11761 | 0.11689 | 2.1554 | 2.7493 | 0.49108 | 3.7308
2025-06-16 12:00 | 33.6613 | 6.4928 | 0.92553 | 0.97886 | 21.0589 | 4.3913 | 12.6568 | 192.8018 | 16.2169 | 193.6649 | 27.3776 | 19.1715 | 13.8185 | 197.305 | 30.3064 | 19.0147 | 13.621 | 195.1931 | 19.2001 | 41.9976 | 13.9033 | 195.6276 | 19.7943 | 43.0379 | 13.8687 | 197.136 | 194.4586 | 13.0986 | 44.5745 | 6.7886 | 9.9798 | 0 | 79.8475 | 22.0065 | 50.7233 | 13.3889 | 191.0993 | 194.2937 | 12.9945 | 3.7236 | 52.13 | 95.6856 | 147.8156 | 12.7995 | 134.8772 | 94.6111 | 14.5818 | 7.2472 | 16.2169 | 193.6649 | 90.2294 | 15.349 | 0.89578 | 0.25195 | 91.3015 | 0.11923 | 0.11828 | 2.138 | 0.094018 | 0.46492 | 3.5731
2025-06-16 13:00 | 33.6555 | 6.4622 | 0.9426 | 0.99598 | 21.3822 | 4.3966 | 12.6609 | 192.8218 | 16.2416 | 193.5886 | 27.3247 | 19.1374 | 13.8367 | 197.3577 | 30.319 | 19.0593 | 13.6341 | 195.2405 | 19.1994 | 42.0194 | 13.9152 | 195.7003 | 19.8038 | 43.0312 | 13.8789 | 197.1961 | 194.4909 | 13.1063 | 44.7223 | 6.696 | 9.9801 | 0 | 79.9163 | 22.0042 | 50.6925 | 13.3936 | 191.1172 | 194.3192 | 12.9994 | 3.6877 | 52.5186 | 95.4494 | 147.968 | 12.7976 | 135.0003 | 94.4147 | 14.5823 | 7.2663 | 16.2416 | 193.5886 | 90.1969 | 15.3543 | 0.8865 | 0.23262 | 91.6415 | 0.1184 | 0.11714 | 0.079219 | 0.093278 | 0.48636 | 5.2499
2025-06-16 14:00 | 33.687 | 6.3384 | 0.94711 | 1.0006 | 21.5263 | 4.3958 | 12.7079 | 192.9697 | 16.2355 | 193.655 | 27.3643 | 19.2182 | 13.8861 | 197.4976 | 30.3291 | 19.1225 | 13.6826 | 195.3806 | 19.1696 | 42.0165 | 13.966 | 195.816 | 19.7919 | 43.0286 | 13.9218 | 197.2835 | 194.6393 | 13.1537 | 44.655 | 6.4931 | 9.98 | 0 | 79.9566 | 22.0017 | 50.6804 | 13.437 | 191.2321 | 194.474 | 13.0455 | 3.8085 | 53.0729 | 95.0084 | 148.0813 | 12.7504 | 134.6331 | 94.5449 | 14.5823 | 7.2318 | 16.2355 | 193.655 | 90.6709 | 15.3232 | 0.8982 | 0.22578 | 91.2549 | 0.11503 | 0.11407 | 0.07656 | 0.091302 | 0.53067 | 6.4329
2025-06-16 15:00 | 33.7347 | 6.5146 | 0.9479 | 0.99976 | 21.3652 | 4.3496 | 12.7601 | 193.1349 | 16.2388 | 193.7207 | 27.2694 | 19.6665 | 13.9507 | 197.6605 | 30.3445 | 19.4629 | 13.7355 | 195.5184 | 19.1934 | 42.0142 | 14.0286 | 195.9392 | 19.793 | 42.9826 | 13.9684 | 197.406 | 194.7976 | 13.2052 | 44.6238 | 6.3267 | 9.9796 | 0 | 79.9838 | 22.0029 | 50.4685 | 13.4855 | 191.3444 | 194.635 | 13.0952 | 3.9047 | 52.0792 | 94.6525 | 146.7317 | 12.73 | 134.293 | 95.1716 | 14.5814 | 7.2005 | 16.2388 | 193.7207 | 90.9384 | 15.3109 | 0.92423 | 0.22589 | 90.7488 | 0.11069 | 0.11298 | 4.267 | 0.088346 | 0.58167 | 3.2965
2025-06-16 16:00 | 33.7385 | 6.1267 | 0.9358 | 0.97999 | 20.6367 | 4.3839 | 12.7432 | 193.0768 | 16.383 | 193.7544 | 27.1042 | 19.5551 | 13.927 | 197.6128 | 30.3461 | 19.36 | 13.7132 | 195.4565 | 19.2014 | 42.0153 | 14.0184 | 195.903 | 19.7761 | 42.9381 | 13.9518 | 197.4392 | 194.7394 | 13.1862 | 44.6198 | 6.1773 | 9.9732 | 0 | 79.9158 | 21.9845 | 50.0579 | 13.4581 | 191.2841 | 194.5897 | 13.0772 | 3.7972 | 52.4174 | 95.4879 | 147.9053 | 12.8958 | 135.041 | 95.3062 | 14.5785 | 7.2777 | 16.383 | 193.7544 | 90.5714 | 15.4441 | 0.95416 | 0.23052 | 91.2843 | 0.85227 | 0.11575 | 7.0629 | 0.086722 | 0.60951 | 0.41624
2025-06-16 17:00 | 33.8992 | 6.8325 | 0.91275 | 0.9475 | 19.7376 | 4.3031 | 12.8038 | 193.2963 | 16.3101 | 193.8421 | 27.196 | 19.2769 | 13.9561 | 197.8236 | 30.3347 | 19.1327 | 13.7591 | 195.6471 | 19.1873 | 42.0157 | 14.0638 | 196.0673 | 19.7753 | 42.7012 | 14.006 | 197.6811 | 194.9634 | 13.2458 | 44.5915 | 5.9081 | 9.9706 | 0 | 79.7611 | 21.9651 | 49.3455 | 13.5013 | 191.4464 | 194.8202 | 13.139 | 3.4597 | 51.5509 | 94.3214 | 145.8723 | 12.7857 | 134.4639 | 94.6901 | 14.5764 | 7.1874 | 16.3101 | 193.8421 | 89.9374 | 15.3597 | 0.97584 | 0.23933 | 92.3537 | 1.0507 | 0.12334 | 4.5378 | 0.086395 | 0.61722 | 0.41463
2025-06-16 18:00 | 34.0345 | 7.552 | 0.88737 | 0.92406 | 19.1975 | 4.271 | 12.8374 | 193.4124 | 16.365 | 193.8499 | 27.1594 | 19.2196 | 13.9655 | 197.9207 | 30.3302 | 19.0815 | 13.7794 | 195.7358 | 19.174 | 42.0168 | 14.0846 | 196.129 | 19.7611 | 42.7368 | 14.0366 | 197.7463 | 195.0669 | 13.275 | 44.4396 | 5.7001 | 9.9739 | 0 | 79.5863 | 21.9637 | 49.55 | 13.527 | 191.4908 | 194.9299 | 13.1729 | 3.604 | 50.8746 | 94.4865 | 145.3611 | 12.7919 | 134.5295 | 94.1308 | 14.576 | 7.174 | 16.365 | 193.8499 | 89.4204 | 15.3978 | 0.99022 | 0.24825 | 92.7539 | 0.30673 | 0.12928 | 5.365 | 0.086314 | 0.61969 | 0.41465
2025-06-16 19:00 | 34.1781 | 6.5342 | 0.87722 | 0.90848 | 19.0162 | 4.2594 | 12.8914 | 193.5935 | 16.4317 | 194.0876 | 27.3784 | 17.8831 | 14.0144 | 198.0839 | 30.297 | 19.174 | 13.8413 | 195.9653 | 19.1691 | 42.0073 | 14.1403 | 196.2826 | 19.71 | 43.4697 | 14.1023 | 197.8741 | 195.2454 | 13.3301 | 44.5301 | 5.664 | 9.9696 | 0 | 79.4218 | 21.966 | 48.8116 | 13.5769 | 191.624 | 195.1012 | 13.2252 | 3.8041 | 51.1631 | 94.4166 | 145.5796 | 12.8495 | 134.9412 | 94.467 | 14.5758 | 7.2065 | 16.4317 | 194.0876 | 89.2575 | 15.4507 | 0.99804 | 0.25687 | 92.0986 | 0.10849 | 0.13076 | 5.6233 | 0.086369 | 0.6144 | 0.41571
2025-06-16 20:00 | 34.6468 | 5.3376 | 0.88431 | 0.90716 | 19.0419 | 4.123 | 13.188 | 194.5891 | 16.2699 | 194.6697 | 28.5609 | 14.4071 | 14.2939 | 199.0106 | 29.8493 | 19.7327 | 14.1596 | 197.0692 | 19.1622 | 41.9816 | 14.4321 | 197.1244 | 19.8172 | 44.7077 | 14.4191 | 198.7885 | 196.2705 | 13.6419 | 45.0511 | 5.6613 | 9.9627 | 0 | 79.2805 | 21.982 | 46.6802 | 13.8567 | 192.4064 | 196.0701 | 13.5177 | 3.6149 | 50.9227 | 91.9245 | 142.8472 | 12.6807 | 134.0759 | 94.8549 | 14.5756 | 7.118 | 16.2699 | 194.6697 | 89.2138 | 15.2873 | 1.0016 | 0.2593 | 92.4883 | 0.10872 | 0.12951 | 3.5147 | 0.086569 | 0.60767 | 0.41692
2025-06-16 21:00 | 34.4149 | 4.4402 | 0.87517 | 0.90194 | 18.9574 | 4.2403 | 13.1263 | 194.3519 | 16.6152 | 194.4929 | 28.0857 | 12.1177 | 14.202 | 198.6471 | 29.4395 | 19.9135 | 14.0904 | 196.84 | 19.218 | 41.9717 | 14.3752 | 196.9128 | 19.6921 | 46.0585 | 14.3711 | 198.5643 | 196.0018 | 13.5681 | 44.4844 | 5.6369 | 9.965 | 0 | 79.164 | 22.0162 | 47.8196 | 13.7986 | 192.1558 | 195.8134 | 13.4549 | 3.6701 | 50.3535 | 95.5775 | 145.931 | 12.999 | 135.9062 | 94.7737 | 14.5756 | 7.2847 | 16.6152 | 194.4929 | 89.3644 | 15.6292 | 1.0016 | 0.25743 | 92.8688 | 0.10877 | 0.12799 | 2.7653 | 0.086846 | 0.60412 | 0.41602
2025-06-16 22:00 | 34.2929 | 5.3 | 0.88709 | 0.91155 | 18.7577 | 4.2561 | 12.9282 | 193.6984 | 16.4536 | 194.1792 | 28.4666 | 12.1195 | 14.0171 | 198.0736 | 29.5262 | 19.8661 | 13.8894 | 196.1546 | 19.3334 | 41.9786 | 14.199 | 196.3263 | 19.2847 | 46.0216 | 14.1694 | 197.9915 | 195.3764 | 13.375 | 44.7724 | 5.4995 | 9.9693 | 0 | 79.0424 | 22.0184 | 48.5826 | 13.6137 | 191.662 | 195.1925 | 13.2631 | 3.7952 | 51.8203 | 94.1334 | 145.9537 | 12.8288 | 135.1171 | 95.0718 | 14.5756 | 7.2268 | 16.4536 | 194.1792 | 89.2149 | 15.4669 | 1.0022 | 0.25803 | 91.9602 | 0.10863 | 0.13071 | 1.7052 | 0.086582 | 0.60848 | 0.41365
2025-06-16 23:00 | 34.0842 | 5.5019 | 0.8858 | 0.91382 | 18.6081 | 4.2185 | 12.7998 | 193.3155 | 16.0908 | 194.02 | 28.3623 | 12.1132 | 13.8779 | 197.6874 | 29.6049 | 19.5334 | 13.7552 | 195.7787 | 19.1854 | 41.9832 | 14.0642 | 195.9239 | 19.0704 | 45.8773 | 14.0254 | 197.5015 | 194.9955 | 13.2442 | 44.7847 | 5.4345 | 9.9717 | 0 | 78.9189 | 22.0029 | 49.145 | 13.493 | 191.4037 | 194.8341 | 13.138 | 3.7979 | 51.6726 | 92.111 | 143.7837 | 12.3484 | 133.5935 | 94.4739 | 14.5757 | 6.9813 | 16.0908 | 194.02 | 88.9592 | 15.0891 | 1.0053 | 0.25861 | 91.8523 | 0.10838 | 0.13396 | 0.61621 | 0.08625 | 0.61161 | 0.39348
2025-06-17 | 34.5118 | 3.8791 | 0.81381 | 0.87489 | 17.5411 | 4.1401 | 13.1433 | 194.1664 | 16.3096 | 193.6583 | 27.2708 | 12.0845 | 14.1737 | 198.3473 | 29.6708 | 18.0439 | 14.0603 | 196.4607 | 19.2323 | 41.9882 | 14.3587 | 196.5377 | 19.2677 | 47.0089 | 14.3438 | 197.9965 | 195.7138 | 13.5643 | 43.5514 | 5.4651 | 9.9748 | 0 | 78.8005 | 22.007 | 51.1153 | 13.8071 | 191.3416 | 195.5219 | 13.4701 | 5.1603 | 40.0124 | 102.8715 | 142.8839 | 12.8394 | 136.4302 | 100.2159 | 14.5777 | 7.402 | 16.3096 | 193.6583 | 93.2703 | 15.3324 | 1.0061 | 0.25189 | 90.7325 | 0.85835 | 0.13763 | 0.87212 | 0.86245 | 1.5139 | 1.1135
Total | MW: 816.5732; MVAR: 122.5867; kg/s: 3842009.412; kg/s: 334578.116; kg/s: 4429877.3232; kg/s: 8226705.5879; kg/s: 12656582.9111; kg/s: 11618661.9132
Average | 34.0239 | 5.1078 | 0.89574 | 0.93308 | 19.4132 | 4.306 | 12.8296 | 193.3751 | 16.1594 | 193.8593 | 27.479 | 16.7363 | 13.9465 | 197.8131 | 30.1309 | 18.2747 | 13.7761 | 195.7205 | 19.2056 | 41.9923 | 14.0772 | 196.0339 | 19.8221 | 43.4698 | 14.0372 | 197.6269 | 195.0277 | 13.2691 | 44.4677 | 6.4621 | 9.9724 | 0 | 79.825 | 22.0019 | 49.6434 | 13.5295 | 191.4149 | 194.8715 | 13.1649 | 3.8724 | 51.2717 | 95.2165 | 146.4882 | 12.6719 | 134.4753 | 94.7524 | 14.5773 | 7.1547 | 16.1594 | 193.8593 | 89.8693 | 15.2854 | 0.9825 | 0.26693 | 91.6374 | 0.22063 | 0.12728 | 1.7298 | 0.34189 | 0.79739 | 1.8816
Min | 33.6555 | 2.6315 | 0.81381 | 0.87047 | 17.5411 | 4.123 | 12.6568 | 192.8018 | 15.7159 | 193.5886 | 26.793 | 12.0845 | 13.8185 | 197.305 | 29.4395 | 15.9924 | 13.621 | 195.1931 | 19.1579 | 41.9671 | 13.9033 | 195.6136 | 19.0704 | 41.6991 | 13.8687 | 197.136 | 194.4586 | 13.0986 | 43.5514 | 5.4345 | 9.9627 | 0 | 78.8005 | 21.9637 | 46.6802 | 13.3889 | 191.0993 | 194.2937 | 12.9945 | 3.4597 | 40.0124 | 91.9245 | 142.8472 | 12.2537 | 132.584 | 93.6192 | 14.5746 | 6.934 | 15.7159 | 193.5886 | 88.8997 | 14.9831 | 0.8865 | 0.22578 | 90.6189 | 0.10718 | 0.11298 | 0.068756 | 0.084602 | 0.46492 | 0.39348
Max | 34.6468 | 7.552 | 0.9479 | 1.0006 | 21.5263 | 4.3966 | 13.188 | 194.5891 | 16.6152 | 194.6697 | 28.5609 | 19.6665 | 14.2939 | 199.0106 | 30.3461 | 19.9135 | 14.1596 | 197.0692 | 19.3334 | 42.0261 | 14.4321 | 197.1244 | 20.4109 | 47.0089 | 14.4191 | 198.7885 | 196.2705 | 13.6419 | 45.0511 | 7.3307 | 9.9801 | 0 | 80.9497 | 22.0404 | 51.1153 | 13.8567 | 192.4064 | 196.0701 | 13.5177 | 5.1603 | 53.0729 | 102.8715 | 148.5081 | 12.999 | 136.4302 | 100.2159 | 14.5823 | 7.402 | 16.6152 | 194.6697 | 93.2703 | 15.6292 | 1.0393 | 0.30389 | 92.8688 | 1.0507 | 0.1461 | 7.0629 | 2.7493 | 1.5462 | 6.4329

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1
18 |  | Night | 22:15 | 5.55 | 22.2
19 | 2025-06-10 | Day | 8:55 | 5.69 | 31.6
20 |  | Night | 0:20 | 5.18 | 24.3
21 | 2025-06-11 | Day | 17:00 | 5.07 | 21.6
22 |  | Night | 22:30 | 5.62 | 28.8
23 | 2025-06-12 | Day | 10:10 | 5.08 | 27.3
24 |  | Night | 21:30 | 5.64 | 26.6
25 | 2025-06-13 | Day | 8:40 | 5.11 | 27.1
26 |  | Night | 22:00 | 5.77 | 25.5
27 | 2025-06-14 | Day | 10:00 | 5.55 | 32
28 |  | Night | 22:00 | 5.78 | 28.9
29 | 2025-06-15 | Day | 10:00 | 5.33 | 24.6
30 |  | Night | 23:45 | 5.82 | 30.3
31 | 2025-06-16 | Day | 9:40 | 5.44 | 27.9
32 |  | Night | 23:45 | 5.97 | 23.8
33 | 2025-06-17 | Day
34 |  | Night
35 | 2025-06-18 | Day
36 |  | Night
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-16
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0