## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-17
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 27.479 | 197.8131 | 16.7363
|  | #6-2 | Production | 30.1309 | 195.7205 | 18.2747
|  | #6-3 | Production | 19.2056 | 196.0339 | 41.9923
|  | #6-4 | Production | 19.8221 | 197.6269 | 43.4698
|  | #8-1 | Shut in | 6.4621 | 79.825 | 9.9724
|  | #8-2 | Production | 22.0019 | 191.4149 | 49.6434
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 44.4677 | 3842009.412
|  | PAD #8 - STEAM |  |  |  |  | 3.8724 | 334578.116 | Online
|  | BRINE HEADER |  |  |  |  | 95.2165 | 8226705.5879 | Offline
|  | TOTAL FLOW |  |  |  |  | 143.5566 | 12403293.116
|  | PRESS SEPARATOR IJN 6 | Online | 13.2691 | 195.0277
|  | PRESS SEPARATOR IJN 8 | Online | 13.1649 | 194.8715
| INJECTION WELL | #5-1 | Injection | 7.1547 | 94.7524 | 14.5773 | 134.4753 | 11684811.1976
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.0239 |  |  | 816.5732
|  | NET | 31.3665 |  |  | 752.795
| PARASITIC LOAD |  | 2.6574 |  |  | 63.7782
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 4.2193 |  |  | 15189.4443
|  | NET | 4.5768 |  |  | 16476.3234
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 6. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
7. Brine Dump Control valve Ijen-6 PV-2227A indication passing
8. Compressor A have indication noise on bearing screw pump
Note on H23: Operator MPGS: - Power meter U3B already reading on 17 June 2025. So the initial value on U3B (Sheet Meter) at 3 Millions following U3A

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-17
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 752794.9561 |  | 0 |  | 752794.9561
|  |  |  | 752794.9561 |  | 0 |  | 752794.9561
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 744590 | [7 empty] | 744590
M-T-D GROSS GENERATION (kWHR) |  |  |  | 14034628 | [7 empty] | 14034628
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18282.25 | 3361563.06 | 4173.38 | 43.3 | 830 | 817 | 24145.93
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 311722.91 | 3078308.76 | 88561.97 | 740.7 | 19917 | 23096 | 132315.67
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.0239 |  |  | 5.1078 |  | 19.4132
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 408
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 90.93%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 3852.3884 |  | 309.108 |  |  | 4419.4609
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.044468 |  | 0.0038724 |  |  | 0.051272
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 8208.963
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.095216
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 12628.424
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.14649
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 193.3751 |  |  |  | 193.8593
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.8296 |  |  |  | 16.1594
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 17.5411 |  | 21.5263 |  |  | 19.4132
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
6. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
7. Brine Dump Control valve Ijen-6 PV-2227A indication passing
8. Compressor A have indication noise on bearing screw pump
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:40 | Update inlet pH brine+condensate inlet preheater (pH : 5.97 and Temperature : 23.8 degC)
7:45 | Handover night shift to day shift
8:10 | Daily toolbox meeting and safety talk
9:30 | Continue cleaning on strainer reinjection pump A
10:53 | Run test and check on diesel pit pump IJN 6 due to leaks on mechseal, discharge pressure 17.5 barg. Result: top ring is going down, tomorrow will rectify by maintenance team and IKPT.
14:20 | Check and Release Pressure & Condensate Master Valve & Wing Valve PW IJN 6-1. Result: Normal [Standard Activity]
14:22 | Run test and close monitoring on GCW pump A due to bearing oil leaks. Now still running with GCW pump A and still under monitoring until tomorrow
15:10 | EDG unload Test Run [Standard activity]
15:26 | Check on condensate pump B performance with Mr. Ardhiya
16:10 | U3B power meter has been fixed (by Mr. Rodhel) and readable on local and HMI (Oneline). Troible: failed on IP address
16:20 | Inspection of Main Transformers (GSUT). Result: Normal [Standard activity]
16:30 | Inspection of Switchyard Equipment. Result: Normal [Standard activity]
22:31 | Increase pressure plan 53B of Reinjection Pump-B from 2 Bar to 12 Bar
22:37 | Check oil leak at Generator Cooling Water (GCW) Pump - A --> Result : Not found oil leak
22:45 | Update inlet pH brine+condensate inlet preheater (pH : 5.86 and Temperature : 27.7 degC)
22:51 | Increase pressure plan 53B of Condensate pump-A from 3 Bar to 13 Bar
IX.) SERVICE REQUEST
SR-06-2025-0010 | Level on LT-2301A and LT-2301B (Brine Accumulator) IJN-8 has difference around 10%
X.) SHIFT CREW
Day Shift | Shift Leader : Hary |  |  |  | CCR Operator : Fauzan |  |  |  | Steamfield : Vandy
Night Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Dwiki |  |  |  | Steamfield : Rafly
Note on H13: Operator MPGS: - Power meter already reading on 17 June 2025 - Initial value following U3A on 3 Millions

## Meter
DATE: | 2025-06-17
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2226060 | 2238440 | 12380 | 110590
(BACKUP) |  | 2126290 | 2224390 | 2236750 | 12360 | 110460
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 105268320 | 106012910 | 744590 | 12911000
(BACKUP) |  | 93082960 | 105245920 | 105990300 | 744380 | 12907340
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4690720 | 4703140 | 12420 | 560910
(BACKUP) |  | 4144060 | 4692710 | 4705130 | 12420 | 561070
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 114550106 | 115357883 | 807777 | 14034628
TOTAL |  |  |  |  | 807777 | 14034628
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 18784768 | 18893052 | 108284 | 2362797
TOTAL |  |  |  |  | 108284 | 2362797
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3382759 | 3401041.25 | 18282.25 | 311722.91
U3B |  | 283254.3 |  | 3361563.06 | 3361563.06 | 3078308.76
U3C |  | 989758.41 | 1074147 | 1078320.38 | 4173.38 | 88561.97
U Ijen 5 |  | 7258.6 | 7956 | 7999.3 | 43.3 | 740.7
U Ijen 6 |  | 247889 | 266976 | 267806 | 830 | 19917
U Ijen 8 |  | 299837 | 322116 | 322933 | 817 | 23096
TOTAL |  |  |  |  | 3385708.99 | 444038.58
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power meter already reading on 17 June 2025
Note on G43: Operator MPGS: - Power meter already reading on 17 June 2025 - Initial value following U3A on 3 Millions

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-17 01:00 | 34.1829 | 4.0448 | 0.87475 | 0.90845 | 18.2876 | 4.192 | 12.7229 | 193.0527 | 15.9905 | 193.8264 | 28.5823 | 12.0841 | 13.7964 | 197.4501 | 29.6013 | 17.9885 | 13.6714 | 195.5076 | 19.1655 | 41.9876 | 13.9853 | 195.7473 | 18.9921 | 45.8099 | 13.9448 | 197.4479 | 194.7281 | 13.1628 | 44.963 | 5.6351 | 9.9732 | 0 | 78.6964 | 21.9509 | 51.1727 | 13.4186 | 191.1118 | 194.5312 | 13.0618 | 3.7426 | 50.1996 | 93.0955 | 143.2951 | 12.2939 | 134.0755 | 95.0306 | 14.5752 | 7.054 | 15.9905 | 193.8264 | 89.1764 | 14.9879 | 1.0053 | 0.25784 | 92.8841 | 0.10661 | 0.15245 | 0.095916 | 0.08453 | 0.64358 | 1.8546
2025-06-17 02:00 | 33.9085 | 4.0192 | 0.8532 | 0.88855 | 18.2277 | 4.2699 | 12.6225 | 192.6915 | 15.977 | 193.4156 | 28.2265 | 12.0855 | 13.6746 | 197.0229 | 29.6069 | 17.988 | 13.5553 | 195.1257 | 19.141 | 41.9883 | 13.8722 | 195.437 | 18.9097 | 45.0592 | 13.8222 | 197.1194 | 194.3297 | 13.0492 | 44.2191 | 5.8139 | 9.9734 | 0 | 78.5837 | 21.9313 | 51.1824 | 13.32 | 190.7955 | 194.1772 | 12.9609 | 3.5533 | 49.9055 | 94.8821 | 144.7876 | 12.3188 | 134.6189 | 95.1398 | 14.5748 | 7.0535 | 15.977 | 193.4156 | 89.6282 | 14.9655 | 1.0052 | 0.25707 | 93.4183 | 0.1065 | 0.15631 | 0.23399 | 0.084471 | 0.6425 | 1.3583
2025-06-17 03:00 | 33.9923 | 3.5977 | 0.851 | 0.88956 | 18.0277 | 4.2547 | 12.6244 | 192.6806 | 15.988 | 193.3558 | 29.0123 | 12.0853 | 13.693 | 197.0899 | 29.6322 | 17.9889 | 13.567 | 195.1573 | 19.1015 | 41.9892 | 13.8814 | 195.4599 | 19.0165 | 45.0612 | 13.8397 | 197.1328 | 194.3439 | 13.0595 | 44.5987 | 5.8731 | 9.9733 | 0 | 78.4617 | 21.9134 | 51.1936 | 13.3229 | 190.78 | 194.1739 | 12.9647 | 3.5686 | 50.1191 | 94.5067 | 144.6258 | 12.353 | 134.5532 | 95.2283 | 14.5746 | 7.0917 | 15.988 | 193.3558 | 89.6299 | 14.9645 | 1.0032 | 0.26231 | 93.8633 | 0.1065 | 0.15681 | 0.23407 | 0.084508 | 0.64145 | 1.3737
2025-06-17 04:00 | 33.7928 | 4.1708 | 0.86336 | 0.89849 | 17.9363 | 4.2425 | 12.5905 | 192.5901 | 16.0577 | 193.4713 | 28.3601 | 12.0827 | 13.6546 | 196.9704 | 29.6566 | 17.9881 | 13.5307 | 195.0564 | 19.0501 | 41.9892 | 13.8455 | 195.3699 | 19.0652 | 45.3097 | 13.8119 | 197.0156 | 194.2459 | 13.0219 | 44.4728 | 5.8668 | 9.9721 | 0 | 78.3436 | 21.9056 | 51.1854 | 13.293 | 190.7328 | 194.0837 | 12.9308 | 3.5182 | 48.9147 | 94.4518 | 143.3665 | 12.2932 | 134.2619 | 94.7483 | 14.5744 | 7.0145 | 16.0577 | 193.4713 | 89.3194 | 15.0118 | 0.99593 | 0.26858 | 93.7391 | 0.10674 | 0.15422 | 0.62745 | 0.084778 | 0.63075 | 0.98947
2025-06-17 05:00 | 33.9187 | 4.1071 | 0.87051 | 0.90405 | 17.967 | 4.2616 | 12.6097 | 192.6705 | 16.2839 | 193.4983 | 28.4064 | 12.0814 | 13.6803 | 197.0491 | 29.667 | 17.9867 | 13.5552 | 195.1151 | 19.0893 | 41.9887 | 13.8703 | 195.4543 | 19.0267 | 45.5419 | 13.837 | 197.0618 | 194.3332 | 13.0437 | 44.5175 | 5.8565 | 9.9705 | 0 | 78.242 | 21.9053 | 51.1791 | 13.3126 | 190.7863 | 194.1664 | 12.9498 | 3.564 | 49.2018 | 95.3452 | 144.547 | 12.4676 | 134.817 | 94.6264 | 14.5741 | 7.1161 | 16.2839 | 193.4983 | 89.489 | 15.2211 | 0.99091 | 0.26785 | 93.3162 | 0.10695 | 0.15133 | 0.62793 | 0.084931 | 0.62025 | 1.1673
2025-06-17 06:00 | 33.9727 | 2.9988 | 0.87018 | 0.90597 | 18.2434 | 4.2352 | 12.5984 | 192.6137 | 16.1691 | 193.2973 | 28.5588 | 12.0763 | 13.6605 | 196.9677 | 29.6652 | 17.9879 | 13.5412 | 195.0765 | 19.0717 | 41.9903 | 13.8494 | 195.4024 | 18.9514 | 45.5358 | 13.8202 | 196.9781 | 194.2818 | 13.0325 | 44.5573 | 5.9631 | 9.9732 | 0 | 78.1695 | 21.9041 | 51.1846 | 13.3051 | 190.7303 | 194.1105 | 12.939 | 3.5453 | 49.1234 | 94.7566 | 143.88 | 12.4088 | 134.439 | 94.8795 | 14.5745 | 7.0869 | 16.1691 | 193.2973 | 89.6249 | 15.1075 | 0.98502 | 0.26786 | 93.213 | 0.10721 | 0.14847 | 0.40123 | 0.085569 | 0.61942 | 1.2678
2025-06-17 07:00 | 33.8401 | 3.785 | 0.87625 | 0.91042 | 18.6576 | 4.2565 | 12.5493 | 192.4408 | 16.12 | 193.1076 | 28.4673 | 12.0607 | 13.6176 | 196.7709 | 29.6631 | 17.9938 | 13.4941 | 194.9315 | 19.0772 | 41.9915 | 13.7977 | 195.2782 | 18.9134 | 45.5412 | 13.7717 | 196.7773 | 194.1057 | 12.9828 | 44.4776 | 5.9904 | 9.9751 | 0 | 78.1156 | 21.9072 | 51.1641 | 13.263 | 190.5881 | 193.9317 | 12.8899 | 3.5248 | 48.9008 | 95.1398 | 144.0406 | 12.4448 | 134.8714 | 95.5121 | 14.5754 | 7.1309 | 16.12 | 193.1076 | 89.885 | 15.0601 | 0.95719 | 0.26286 | 94.0359 | 0.10854 | 0.13457 | 0.40272 | 0.086945 | 0.61058 | 1.264
2025-06-17 08:00 | 33.7262 | 5.153 | 0.88753 | 0.92338 | 19.1394 | 4.254 | 12.5523 | 192.4524 | 16.0232 | 193.3649 | 28.7994 | 12.2906 | 13.6392 | 196.7997 | 29.6753 | 18.0027 | 13.5029 | 194.9451 | 19.0096 | 42.4451 | 13.7956 | 195.3315 | 18.8839 | 45.444 | 13.7762 | 196.8056 | 194.1197 | 12.9893 | 44.6066 | 5.9007 | 9.975 | 0 | 78.078 | 21.9116 | 51.1634 | 13.2698 | 190.6285 | 193.9296 | 12.8921 | 3.4623 | 49.3258 | 94.1445 | 143.4703 | 12.3453 | 134.4323 | 95.5802 | 14.5757 | 7.0768 | 16.0232 | 193.3649 | 89.7239 | 14.9517 | 0.91328 | 0.2602 | 94.2291 | 0.11024 | 0.11872 | 0.49356 | 0.088662 | 0.59311 | 1.0722
2025-06-17 09:00 | 33.7088 | 5.988 | 0.90292 | 0.94441 | 19.7243 | 4.4242 | 12.5554 | 192.4755 | 16.2928 | 193.4302 | 28.5638 | 12.8093 | 13.6549 | 196.8173 | 29.7041 | 17.8829 | 13.5164 | 194.9829 | 19.0566 | 43.4483 | 13.8228 | 195.545 | 18.8604 | 45.2236 | 13.7843 | 196.8846 | 194.1506 | 12.9965 | 44.606 | 5.9936 | 9.975 | 0 | 78.1216 | 21.9301 | 51.1572 | 13.279 | 190.7038 | 193.9534 | 12.8945 | 3.4399 | 53.7107 | 95.4254 | 149.136 | 12.5957 | 135.8636 | 95.185 | 14.5762 | 7.2235 | 16.2928 | 193.4302 | 89.9375 | 15.1921 | 0.86162 | 0.23996 | 94.3177 | 0.11213 | 0.11246 | 0.87712 | 0.090981 | 0.55078 | 0.85879
2025-06-17 10:00 | 33.6039 | 5.6372 | 0.91671 | 0.9653 | 20.3434 | 4.4563 | 12.5642 | 192.4993 | 16.0979 | 193.4039 | 28.7097 | 13.2499 | 13.6798 | 196.8478 | 29.8086 | 17.8338 | 13.5302 | 194.9735 | 18.8633 | 44.1643 | 13.8376 | 195.5718 | 18.9089 | 45.0949 | 13.7893 | 196.8727 | 194.1797 | 13.0091 | 44.5907 | 5.7782 | 9.9752 | 0 | 78.2469 | 21.9465 | 51.1397 | 13.295 | 190.7716 | 193.9809 | 12.9026 | 3.5324 | 55.8651 | 93.8824 | 149.7474 | 12.3679 | 134.8014 | 95.279 | 14.5834 | 7.1178 | 16.0979 | 193.4039 | 90.2268 | 15.0043 | 0.82315 | 0.21486 | 93.998 | 0.11405 | 0.11143 | 0.82784 | 0.092827 | 0.5067 | 0.97702
2025-06-17 11:00 | 33.699 | 4.121 | 0.93245 | 0.9899 | 20.9179 | 4.4239 | 12.6966 | 192.9167 | 16.2791 | 193.5142 | 28.4665 | 14.9349 | 13.8492 | 197.3189 | 29.8323 | 19.594 | 13.6907 | 195.4552 | 18.6598 | 44.8022 | 13.9821 | 195.9194 | 19.0033 | 45.2188 | 13.9339 | 197.2792 | 194.5986 | 13.1469 | 44.7965 | 5.2216 | 9.9807 | 0 | 78.4156 | 21.9562 | 50.5414 | 13.4262 | 191.1514 | 194.3886 | 13.0321 | 3.6483 | 54.4277 | 94.6542 | 149.0819 | 12.4767 | 135.677 | 95.2857 | 14.5911 | 7.1733 | 16.2791 | 193.5142 | 90.5951 | 15.1577 | 0.80137 | 0.20835 | 94.051 | 0.11596 | 0.11258 | 1.8255 | 0.093716 | 0.48144 | 1.4243
2025-06-17 12:00 | 34.147 | 3.9617 | 0.92519 | 0.97688 | 20.7818 | 4.4729 | 12.8029 | 193.2637 | 16.7733 | 193.8576 | 27.9549 | 16.1295 | 14.0018 | 197.7633 | 29.5863 | 20.9823 | 13.8386 | 195.9646 | 18.6269 | 45.1475 | 14.1168 | 196.3271 | 18.9842 | 45.2262 | 14.059 | 197.6862 | 194.9699 | 13.2614 | 45.1394 | 5.0165 | 9.9844 | 0 | 78.5659 | 21.9584 | 49.5155 | 13.5218 | 191.4685 | 194.7475 | 13.134 | 3.8247 | 55.3536 | 97.3819 | 152.7355 | 12.9757 | 137.9336 | 95.8333 | 14.6015 | 7.4948 | 16.7733 | 193.8576 | 90.795 | 15.6008 | 0.79536 | 0.1962 | 94.8607 | 0.11636 | 0.11298 | 2.6348 | 0.093439 | 0.47125 | 1.8524
2025-06-17 13:00 | 34.3145 | 5.0374 | 0.87688 | 0.90643 | 20.0527 | 4.3587 | 12.8573 | 193.4794 | 16.5114 | 194.175 | 28.5602 | 14.2638 | 14.0248 | 197.9318 | 29.4552 | 19.1547 | 13.8654 | 196.0967 | 18.4921 | 45.024 | 14.1312 | 196.3967 | 18.9531 | 45.0986 | 14.0889 | 197.8083 | 195.1645 | 13.309 | 44.9171 | 4.8721 | 9.9796 | 0 | 78.6396 | 21.9737 | 48.105 | 13.5652 | 191.7056 | 194.977 | 13.1866 | 3.3107 | 54.0538 | 95.5126 | 149.5664 | 12.7137 | 136.3874 | 95.9578 | 14.611 | 7.3568 | 16.5114 | 194.175 | 89.9073 | 15.3397 | 0.8459 | 0.19956 | 94.5315 | 0.11403 | 0.1115 | 1.5198 | 0.091659 | 0.51926 | 1.7853
2025-06-17 14:00 | 34.253 | 5.6348 | 0.84469 | 0.86172 | 19.3543 | 4.2792 | 12.8483 | 193.4682 | 16.3438 | 193.9891 | 28.9332 | 12.1297 | 13.9593 | 197.7854 | 29.6398 | 17.0238 | 13.8152 | 195.971 | 18.5764 | 45.0254 | 14.1104 | 196.3509 | 19.0407 | 45.0942 | 14.0619 | 197.7607 | 195.1196 | 13.29 | 44.5003 | 4.776 | 9.9758 | 0 | 78.7025 | 22.0038 | 48.329 | 13.5535 | 191.7133 | 194.9465 | 13.1787 | 3.1178 | 51.6123 | 94.9624 | 146.5747 | 12.4584 | 135.5713 | 94.8327 | 14.6117 | 7.1653 | 16.3438 | 193.9891 | 89.4353 | 15.1616 | 0.90597 | 0.22733 | 93.6171 | 0.11209 | 0.11049 | 0.86181 | 0.089894 | 0.57977 | 1.5361
2025-06-17 15:00 | 34.1209 | 5.114 | 0.86375 | 0.89376 | 19.046 | 4.2855 | 12.808 | 193.3121 | 16.3064 | 193.7477 | 28.6643 | 13.4599 | 13.914 | 197.6251 | 29.7373 | 18.147 | 13.7757 | 195.8664 | 18.5564 | 45.0225 | 14.0856 | 196.2117 | 19.09 | 45.083 | 14.0267 | 197.6711 | 194.9705 | 13.2501 | 44.5169 | 4.833 | 9.976 | 0 | 78.7322 | 21.9983 | 49.2367 | 13.5079 | 191.5056 | 194.7858 | 13.1406 | 3.4283 | 51.7922 | 94.4342 | 146.2263 | 12.3179 | 134.7486 | 94.9349 | 14.6108 | 7.0719 | 16.3064 | 193.7477 | 89.9115 | 15.101 | 0.91922 | 0.25107 | 93.6142 | 0.11064 | 0.11221 | 1.4415 | 0.088406 | 0.59987 | 1.1609
2025-06-17 16:00 | 34.1662 | 4.2153 | 0.886 | 0.92449 | 18.8985 | 4.3292 | 12.7717 | 193.1717 | 16.5708 | 193.8742 | 28.2807 | 15.2467 | 13.9074 | 197.6411 | 29.4822 | 19.9389 | 13.7697 | 195.8813 | 18.443 | 45.0192 | 14.0696 | 196.114 | 19.0171 | 45.0761 | 14.0118 | 197.5597 | 194.852 | 13.2189 | 44.9489 | 4.9195 | 9.9732 | 0 | 78.6962 | 21.9701 | 49.3547 | 13.4664 | 191.3297 | 194.6454 | 13.1072 | 3.4944 | 52.3548 | 95.5562 | 147.911 | 12.5965 | 135.9148 | 95.8176 | 14.6085 | 7.2283 | 16.5708 | 193.8742 | 89.8686 | 15.3495 | 0.91868 | 0.25074 | 94.3242 | 0.10914 | 0.11825 | 3.7937 | 0.087209 | 0.60513 | 1.1862
2025-06-17 17:00 | 34.1805 | 5.3714 | 0.88019 | 0.91295 | 18.534 | 4.3341 | 12.8159 | 193.3553 | 16.678 | 194.2807 | 27.8562 | 14.7811 | 13.9469 | 197.8475 | 29.2421 | 19.6802 | 13.8153 | 196.1035 | 18.4266 | 45.0135 | 14.1109 | 196.2549 | 18.9631 | 45.073 | 14.0507 | 197.6731 | 195.0346 | 13.2608 | 45.0463 | 5.1749 | 9.9701 | 0 | 78.633 | 21.9543 | 48.4131 | 13.5011 | 191.4969 | 194.8194 | 13.1497 | 3.7416 | 51.5181 | 96.6249 | 148.143 | 12.7725 | 136.7237 | 95.5878 | 14.6071 | 7.3239 | 16.678 | 194.2807 | 89.1578 | 15.4544 | 0.92852 | 0.24434 | 94.3963 | 0.1081 | 0.12962 | 2.9483 | 0.086277 | 0.61218 | 1.792
2025-06-17 18:00 | 34.34 | 6.9407 | 0.8781 | 0.91071 | 18.3788 | 4.281 | 12.8644 | 193.5305 | 16.6757 | 194.1463 | 28.4925 | 13.7942 | 13.9843 | 198.0112 | 29.2256 | 18.6761 | 13.8552 | 196.235 | 18.4919 | 45.0091 | 14.1584 | 196.3871 | 19.0416 | 45.0634 | 14.0965 | 197.8382 | 195.2123 | 13.3103 | 45.1536 | 5.3445 | 9.9704 | 0 | 78.5393 | 21.9637 | 48.2749 | 13.5448 | 191.6014 | 195.0034 | 13.1988 | 3.8429 | 51.0514 | 95.9597 | 147.0111 | 12.7689 | 136.3668 | 95.2236 | 14.6061 | 7.3514 | 16.6757 | 194.1463 | 88.9919 | 15.4434 | 0.9401 | 0.24719 | 93.9272 | 0.10726 | 0.1415 | 2.4136 | 0.085323 | 0.6197 | 1.7616
2025-06-17 19:00 | 34.4041 | 5.724 | 0.86834 | 0.90248 | 18.1173 | 4.2214 | 12.8286 | 193.3805 | 16.4874 | 193.9161 | 29.0089 | 12.6708 | 13.9259 | 197.83 | 29.3363 | 17.5577 | 13.8011 | 196.005 | 18.4434 | 45.008 | 14.1114 | 196.1814 | 19.0503 | 45.0578 | 14.0506 | 197.6568 | 195.0554 | 13.272 | 45.0341 | 5.2639 | 9.9712 | 0 | 78.4294 | 21.9636 | 49.2906 | 13.511 | 191.4126 | 194.8549 | 13.1646 | 3.9315 | 50.9736 | 94.2611 | 145.2347 | 12.4961 | 134.9536 | 95.271 | 14.6055 | 7.1735 | 16.4874 | 193.9161 | 89.0136 | 15.2504 | 0.9451 | 0.24778 | 93.6395 | 0.10678 | 0.15173 | 2.4145 | 0.084852 | 0.62344 | 1.216
2025-06-17 20:00 | 34.2103 | 3.5944 | 0.83482 | 0.87807 | 17.6829 | 4.27 | 12.8332 | 193.3854 | 16.4023 | 193.9356 | 28.7491 | 12.9534 | 13.9031 | 197.7525 | 29.5202 | 17.0618 | 13.7811 | 195.9039 | 18.4142 | 45.008 | 14.095 | 196.1093 | 19.0139 | 45.0555 | 14.0332 | 197.5722 | 195.033 | 13.2677 | 44.5372 | 5.1915 | 9.9712 | 0 | 78.3303 | 21.9567 | 49.4861 | 13.5125 | 191.4146 | 194.8629 | 13.1666 | 3.9265 | 51.5755 | 94.5019 | 146.0775 | 12.3962 | 134.8045 | 95.672 | 14.6049 | 7.0774 | 16.4023 | 193.9356 | 89.0709 | 15.1549 | 0.94702 | 0.24633 | 94.0065 | 0.10667 | 0.15814 | 1.1552 | 0.084781 | 0.62903 | 1.3294
2025-06-17 21:00 | 34.0904 | 3.6651 | 0.82006 | 0.86982 | 17.6163 | 4.224 | 12.7804 | 193.2442 | 16.342 | 193.8517 | 28.9557 | 14.2115 | 13.8525 | 197.6193 | 29.6466 | 16.4297 | 13.724 | 195.7527 | 18.4122 | 45.0071 | 14.0444 | 195.9897 | 19.0071 | 45.0547 | 13.9815 | 197.4583 | 194.8959 | 13.2152 | 44.5264 | 5.2632 | 9.9725 | 0 | 78.2545 | 21.9585 | 49.5486 | 13.4638 | 191.346 | 194.7263 | 13.1152 | 3.7386 | 50.5169 | 93.4815 | 143.9984 | 12.2396 | 134.213 | 95.0435 | 14.6048 | 6.9624 | 16.342 | 193.8517 | 88.4969 | 15.0914 | 0.94853 | 0.25006 | 93.5031 | 0.10664 | 0.15966 | 1.1557 | 0.084754 | 0.63311 | 1.5022
2025-06-17 22:00 | 33.9739 | 4.3769 | 0.83385 | 0.87188 | 17.5743 | 4.1939 | 12.7115 | 193.0125 | 16.3164 | 193.6974 | 28.7448 | 15.1251 | 13.7723 | 197.3635 | 29.8594 | 15.1595 | 13.6374 | 195.4945 | 18.3954 | 45.0065 | 13.969 | 195.7511 | 19.0199 | 45.0527 | 13.9053 | 197.2239 | 194.651 | 13.1404 | 44.3655 | 5.3031 | 9.9735 | 0 | 78.1882 | 21.9533 | 49.7126 | 13.3986 | 191.1271 | 194.4849 | 13.0471 | 3.5992 | 49.2104 | 93.2712 | 142.4816 | 12.1938 | 134.0313 | 94.8344 | 14.605 | 6.9381 | 16.3164 | 193.6974 | 88.5399 | 15.055 | 0.94962 | 0.25181 | 93.413 | 0.10642 | 0.16304 | 0.83999 | 0.084549 | 0.63417 | 1.1915
2025-06-17 23:00 | 33.7986 | 3.5162 | 0.83577 | 0.85997 | 17.0737 | 4.2236 | 12.6538 | 192.803 | 16.2819 | 193.6192 | 28.0601 | 16.3315 | 13.706 | 197.1357 | 30.1206 | 13.5502 | 13.556 | 195.2647 | 18.3526 | 45.0055 | 13.8997 | 195.5186 | 19.0089 | 45.0497 | 13.8334 | 196.9726 | 194.4221 | 13.0745 | 43.9797 | 5.4497 | 9.9719 | 0 | 78.109 | 21.9351 | 50.2093 | 13.34 | 190.9287 | 194.2817 | 12.9887 | 3.5701 | 49.2335 | 93.5182 | 142.7516 | 12.1943 | 134.0004 | 95.6826 | 14.6047 | 6.9535 | 16.2819 | 193.6192 | 88.9856 | 15.0082 | 0.95299 | 0.24792 | 94.0847 | 0.10611 | 0.17111 | 0.8401 | 0.084211 | 0.6401 | 0.773
2025-06-18 | 33.9336 | 2.8167 | 0.83084 | 0.83961 | 16.3039 | 4.397 | 12.5081 | 192.2857 | 17.0951 | 193.6635 | 27.6877 | 17.8971 | 13.5846 | 196.5786 | 30.2747 | 12.0336 | 13.399 | 194.7587 | 18.2504 | 45.0034 | 13.7589 | 195.1543 | 18.9344 | 45.0463 | 13.6895 | 196.4514 | 193.8039 | 12.9031 | 43.0366 | 5.8923 | 9.9762 | 0 | 78.0133 | 21.9229 | 50.2557 | 13.1941 | 190.493 | 193.7743 | 12.8443 | 3.2374 | 48.6877 | 100.5178 | 149.2054 | 12.8965 | 137.7207 | 90.5049 | 14.6037 | 7.3519 | 17.0951 | 193.6635 | 88.0474 | 15.7596 | 0.96095 | 0.24361 | 89.2903 | 0.1059 | 0.17708 | 5.4539 | 0.083918 | 0.64769 | 0.45118
Total | MW: 816.2789; MVAR: 107.5911; kg/s: 3852388.3512; kg/s: 309108.0437; kg/s: 4419460.9223; kg/s: 8208963.0292; kg/s: 12628423.9514; kg/s: 11684811.1976
Average | 34.0239 | 5.1078 | 0.89574 | 0.93308 | 19.4132 | 4.306 | 12.8296 | 193.3751 | 16.1594 | 193.8593 | 27.479 | 16.7363 | 13.9465 | 197.8131 | 30.1309 | 18.2747 | 13.7761 | 195.7205 | 19.2056 | 41.9923 | 14.0772 | 196.0339 | 19.8221 | 43.4698 | 14.0372 | 197.6269 | 195.0277 | 13.2691 | 44.4677 | 6.4621 | 9.9724 | 0 | 79.825 | 22.0019 | 49.6434 | 13.5295 | 191.4149 | 194.8715 | 13.1649 | 3.8724 | 51.2717 | 95.2165 | 146.4882 | 12.6719 | 134.4753 | 94.7524 | 14.5773 | 7.1547 | 16.1594 | 193.8593 | 89.8693 | 15.2854 | 0.9825 | 0.26693 | 91.6374 | 0.22063 | 0.12728 | 1.7298 | 0.34189 | 0.79739 | 1.8816
Min | 33.6555 | 2.6315 | 0.81381 | 0.87047 | 17.5411 | 4.123 | 12.6568 | 192.8018 | 15.7159 | 193.5886 | 26.793 | 12.0845 | 13.8185 | 197.305 | 29.4395 | 15.9924 | 13.621 | 195.1931 | 19.1579 | 41.9671 | 13.9033 | 195.6136 | 19.0704 | 41.6991 | 13.8687 | 197.136 | 194.4586 | 13.0986 | 43.5514 | 5.4345 | 9.9627 | 0 | 78.8005 | 21.9637 | 46.6802 | 13.3889 | 191.0993 | 194.2937 | 12.9945 | 3.4597 | 40.0124 | 91.9245 | 142.8472 | 12.2537 | 132.584 | 93.6192 | 14.5746 | 6.934 | 15.7159 | 193.5886 | 88.8997 | 14.9831 | 0.8865 | 0.22578 | 90.6189 | 0.10718 | 0.11298 | 0.068756 | 0.084602 | 0.46492 | 0.39348
Max | 34.6468 | 7.552 | 0.9479 | 1.0006 | 21.5263 | 4.3966 | 13.188 | 194.5891 | 16.6152 | 194.6697 | 28.5609 | 19.6665 | 14.2939 | 199.0106 | 30.3461 | 19.9135 | 14.1596 | 197.0692 | 19.3334 | 42.0261 | 14.4321 | 197.1244 | 20.4109 | 47.0089 | 14.4191 | 198.7885 | 196.2705 | 13.6419 | 45.0511 | 7.3307 | 9.9801 | 0 | 80.9497 | 22.0404 | 51.1153 | 13.8567 | 192.4064 | 196.0701 | 13.5177 | 5.1603 | 53.0729 | 102.8715 | 148.5081 | 12.999 | 136.4302 | 100.2159 | 14.5823 | 7.402 | 16.6152 | 194.6697 | 93.2703 | 15.6292 | 1.0393 | 0.30389 | 92.8688 | 1.0507 | 0.1461 | 7.0629 | 2.7493 | 1.5462 | 6.4329

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1
18 |  | Night | 22:15 | 5.55 | 22.2
19 | 2025-06-10 | Day | 8:55 | 5.69 | 31.6
20 |  | Night | 0:20 | 5.18 | 24.3
21 | 2025-06-11 | Day | 17:00 | 5.07 | 21.6
22 |  | Night | 22:30 | 5.62 | 28.8
23 | 2025-06-12 | Day | 10:10 | 5.08 | 27.3
24 |  | Night | 21:30 | 5.64 | 26.6
25 | 2025-06-13 | Day | 8:40 | 5.11 | 27.1
26 |  | Night | 22:00 | 5.77 | 25.5
27 | 2025-06-14 | Day | 10:00 | 5.55 | 32
28 |  | Night | 22:00 | 5.78 | 28.9
29 | 2025-06-15 | Day | 10:00 | 5.33 | 24.6
30 |  | Night | 23:45 | 5.82 | 30.3
31 | 2025-06-16 | Day | 9:40 | 5.44 | 27.9
32 |  | Night | 23:45 | 5.97 | 23.8
33 | 2025-06-17 | Day | 15:30 | 5.77 | 33
34 |  | Night | 22:45 | 5.86 | 27.7
35 | 2025-06-18 | Day
36 |  | Night
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-17
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0