## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-18
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 28.2014 | 197.475 | 17.6697
|  | #6-2 | Production | 31.2219 | 195.464 | 11.0115
|  | #6-3 | Production | 18.3582 | 195.7895 | 45.029
|  | #6-4 | Production | 18.9455 | 197.2881 | 45.072
|  | #8-1 | Shut in | 4.2946 | 78.7193 | 9.9734
|  | #8-2 | Production | 21.9389 | 191.2794 | 49.7185
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 43.8179 | 3785865.4298
|  | PAD #8 - STEAM |  |  |  |  | 3.3621 | 290484.2697 | Online
|  | BRINE HEADER |  |  |  |  | 93.291 | 8060346.1953 | Offline
|  | TOTAL FLOW |  |  |  |  | 140.471 | 12136695.8948
|  | PRESS SEPARATOR IJN 6 | Online | 13.1576 | 194.6829
|  | PRESS SEPARATOR IJN 8 | Online | 13.0652 | 194.5306
| INJECTION WELL | #5-1 | Injection | 6.805 | 95.4446 | 14.6083 | 134.2048 | 11595293.0121
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 33.9906 |  |  | 815.7743
|  | NET | 31.3969 |  |  | 753.5262
| PARASITIC LOAD |  | 2.5937 |  |  | 62.248
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 4.1326 |  |  | 14877.5171
|  | NET | 4.474 |  |  | 16106.5339
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 6. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
7. Brine Dump Control valve Ijen-6 PV-2227A indication passing
8. Compressor A have indication noise on bearing screw pump

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-18
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 753526.2373 |  | 0 |  | 753526.2373
|  |  |  | 753526.2373 |  | 0 |  | 753526.2373
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 753960 | [7 empty] | 753960
M-T-D GROSS GENERATION (kWHR) |  |  |  | 14852786 | [7 empty] | 14852786
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18224.34 | 27047.78 | 4108.78 | 42.3 | 812 | 794 | 23981.42
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 329947.25 | 3105356.54 | 92670.75 | 783 | 20729 | 23890 | 138072.75
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 33.9906 |  |  | 5.2779 |  | 16.84
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 432
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 91.02%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 3785.8654 |  | 290.4843 |  |  | 4290.7582
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.043818 |  | 0.0033621 |  |  | 0.049662
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 8060.3462
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.093291
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 12351.1044
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.14295
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 193.0735 |  |  |  | 193.7355
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.7349 |  |  |  | 16.0819
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 13.73 |  | 19.546 |  |  | 16.84
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
6. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
7. Brine Dump Control valve Ijen-6 PV-2227A indication passing
8. Compressor A have indication noise on bearing screw pump
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:31 | increase pressure plan 53B of brine booster pump IJN-6B from 0 Bar to 3 Bars --> When increasing at 10 Bars, pressure drop to 3 Bars
0:35 | Top up barel of plan 53B brine booster pump IJN-6B from 50% to 100%
6:12 | Check and Release Pressure & Condensate Master Valve & Wing Valve PW IJN 6-2, 6-3, 6-4 [Standard Activity]
7:45 | Handover night shift to day shift
8:10 | Daily toolbox meeting and safety talk
9:00 | Enviro division continue monitoring on IJN 6 (Install HVAS)
9:15 | Install strainer reinjection pump A after cleaning.
10:00 | Master valve PW IJN 8-2 exercise 10 rotates, result: normal [Standard Activity]
10:30 | Rectify diesel pit pump IJN 6 by IKPT due to mechseal leaks. Result: still found small leaks but confirmed by maintenance (Mr. Bayu)
10:53 | Switch reinjection pump A after strainer cleaning. Tomorrow will cleaning strainer reinjection pump B because high PDT (0.6 barg)
11:03 | Open CB (LOTO) and rack out pump and fan reinjection pump B due to prepare strainer B cleaning
11:06 | Close and LOTO HV-2624 (Valve before ST-2601B) and HV-2618 (Valve discharge rjc pump B) due to prepare strainer B cleaning
11:28 | Re-Grease DE at FEED Pump A/B/C by maintenance, result report has been emailed by Mr. Baihaqi
14:00 | Check on sand filter with maintenance due to can't auto when receive water. Finding: PT8051 still close. Action: Open PT8051. For the next service water filling, pleace make sure sand filter can auto mode.
14:36 | P8201 Service water Supply Pump run test and switch over from B to A. Close discharge valve B. Discharge pressure before: 4.4 barg / after: 4.7 barg [Standard Activity]
15:00 | Check and Release Pressure & Condensate Master Valve & Wing Valve PW IJN 8-2 [Standard activity]
15:05 | Drain Suction Strainer Booster Pump A IJN 8, result: normal and no passing [Standard activity]
15:15 | Drain Suction Strainer Booster Pump A IJN 6, result: small leaks on suction [Standard activity]
15:50 | Drain Brine Manifold Strainer A SP2501 [Standard activity]
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Hary |  |  |  | CCR Operator : Fauzan |  |  |  | Steamfield : Vandy
Night Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Dwiki |  |  |  | Steamfield : Rafly

## Meter
DATE: | 2025-06-18
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2238440 | 2245040 | 6600 | 117190
(BACKUP) |  | 2126290 | 2236750 | 2243340 | 6590 | 117050
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 106012910 | 106766870 | 753960 | 13664960
(BACKUP) |  | 93082960 | 105990300 | 106744040 | 753740 | 13661080
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4703140 | 4728350 | 25210 | 586120
(BACKUP) |  | 4144060 | 4705130 | 4730360 | 25230 | 586300
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 115357883 | 116176041 | 818158 | 14852786
TOTAL |  |  |  |  | 818158 | 14852786
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 18893052 | 19020822 | 127770 | 2490567
TOTAL |  |  |  |  | 127770 | 2490567
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3401041.25 | 3419265.59 | 18224.34 | 329947.25
U3B |  | 283254.3 | 3361563.06 | 3388610.84 | 27047.78 | 3105356.54
U3C |  | 989758.41 | 1078320.38 | 1082429.16 | 4108.78 | 92670.75
U Ijen 5 |  | 7258.6 | 7999.3 | 8041.6 | 42.3 | 783
U Ijen 6 |  | 247889 | 267806 | 268618 | 812 | 20729
U Ijen 8 |  | 299837 | 322933 | 323727 | 794 | 23890
TOTAL |  |  |  |  | 51029.2 | 468020
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power meter already reading on 17 June 2025 - Initial value following U3A on 3 Millions
Note on G43: Operator MPGS: - Power meter already reading on 17 June 2025 - Initial value following U3A on 3 Millions

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Brine |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater |  | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Brine Header Pressure | Brine Header Temperature | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Delta Pressure | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | barg | oC | oC | Bara | % | % | Barg | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | PT-2503 | TT-2502 | TT-2601 | PT-2603 | PV-2503A | PV-2503B | PV-2503 | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-18 01:00 | 33.9864 | 3.0717 | 0.82123 | 0.82418 | 15.4657 | 4.2051 | 12.6956 | 192.9447 | 16.3925 | 193.6255 | 27.8704 | 17.9908 | 13.7628 | 197.3136 | 30.4151 | 11.967 | 13.5856 | 195.4182 | 18.3362 | 45.003 | 13.9406 | 195.599 | 18.9559 | 45.0517 | 13.8698 | 197.1112 | 194.5466 | 13.1133 | 43.8153 | 5.9516 | 9.9684 | 0 | 77.8966 | 21.9124 | 50.0818 | 13.371 | 190.9884 | 194.4155 | 13.0294 | 3.592 | 48.194 | 94.7238 | 142.9178 | 12.3306 | 134.9224 | 94.7409 | 14.6041 | 7.0278 | 16.3925 | 193.6255 | 88.7221 | 15.0799 | 0.96805 | 0.2397 | 1.3108 | 93.7637 | 0.10557 | 0.19113 | 1.1926 | 0.083658 | 0.64474 | 0.8595
2025-06-18 02:00 | 34.0968 | 3.305 | 0.81481 | 0.81207 | 14.9266 | 4.1051 | 12.7641 | 193.1899 | 16.1937 | 193.7574 | 27.944 | 17.9954 | 13.8212 | 197.5489 | 30.5797 | 11.9704 | 13.6461 | 195.5507 | 18.3263 | 45.0027 | 14 | 195.764 | 18.9594 | 45.065 | 13.9302 | 197.3584 | 194.799 | 13.1841 | 43.8637 | 6.0113 | 9.9692 | 0 | 77.7644 | 21.9084 | 49.8953 | 13.4328 | 191.1747 | 194.6546 | 13.0966 | 3.6375 | 47.8036 | 92.1682 | 139.9718 | 12.0068 | 133.0423 | 95.3681 | 14.6042 | 6.8419 | 16.1937 | 193.7574 | 88.6664 | 14.8676 | 0.97372 | 0.2367 | 1.3242 | 92.9804 | 0.10523 | 0.20206 | 0.65455 | 0.083455 | 0.64434 | 1.1873
2025-06-18 03:00 | 34.1767 | 3.5387 | 0.80184 | 0.79699 | 14.5202 | 4.1342 | 12.8489 | 193.442 | 16.2884 | 193.7903 | 28.264 | 17.9866 | 13.9036 | 197.7833 | 30.6928 | 11.9647 | 13.7228 | 195.6548 | 18.3564 | 45.0028 | 14.0762 | 195.9622 | 18.9867 | 45.0694 | 14.0079 | 197.5683 | 195.0366 | 13.2671 | 43.8118 | 6.0344 | 9.97 | 0 | 77.6436 | 21.9154 | 49.704 | 13.5105 | 191.3343 | 194.8887 | 13.1788 | 3.8325 | 48.1635 | 93.1301 | 141.2935 | 12.0907 | 133.7547 | 95.79 | 14.6045 | 6.8938 | 16.2884 | 193.7903 | 88.8971 | 14.9475 | 0.97613 | 0.23428 | 1.339 | 93.4844 | 0.10501 | 0.20889 | 0.71815 | 0.083352 | 0.64303 | 1.6267
2025-06-18 04:00 | 34.0578 | 4.5792 | 0.75935 | 0.75749 | 13.9433 | 4.1698 | 12.8255 | 193.3895 | 16.4163 | 193.855 | 27.801 | 17.5077 | 13.8648 | 197.6606 | 30.794 | 11.9563 | 13.6884 | 195.6102 | 18.343 | 45.0037 | 14.0432 | 195.911 | 18.9689 | 45.0668 | 13.9763 | 197.4773 | 194.9501 | 13.2331 | 43.2911 | 5.9476 | 9.9696 | 0 | 77.539 | 21.9217 | 49.1953 | 13.4872 | 191.3335 | 194.8382 | 13.1535 | 3.6722 | 47.4492 | 94.5643 | 142.0135 | 12.1419 | 134.481 | 95.2589 | 14.6047 | 6.8798 | 16.4163 | 193.855 | 88.3848 | 15.0538 | 0.97589 | 0.23329 | 1.3608 | 93.7879 | 0.10483 | 0.21225 | 1.145 | 0.083185 | 0.64072 | 1.6765
2025-06-18 05:00 | 34.4136 | 4.9592 | 0.72747 | 0.73287 | 13.73 | 3.9926 | 12.9282 | 193.7634 | 16.1721 | 194.0397 | 28.348 | 17.0396 | 13.9702 | 198.0575 | 30.9016 | 11.9543 | 13.7918 | 196.0106 | 18.3729 | 45.0046 | 14.141 | 196.2214 | 18.9828 | 45.065 | 14.0754 | 197.8252 | 195.3379 | 13.3422 | 43.6967 | 5.9225 | 9.9694 | 0 | 77.4496 | 21.9306 | 48.1163 | 13.5845 | 191.6635 | 195.2108 | 13.255 | 3.1431 | 45.6446 | 91.7559 | 137.4005 | 11.7381 | 132.5243 | 94.6326 | 14.6045 | 6.6271 | 16.1721 | 194.0397 | 87.7366 | 14.8091 | 0.97123 | 0.23551 | 1.3615 | 92.4709 | 0.10496 | 0.21067 | 0.49423 | 0.082811 | 0.63791 | 2.4407
2025-06-18 06:00 | 34.4719 | 4.6338 | 0.72386 | 0.73214 | 14.2377 | 4.0827 | 12.9112 | 193.6532 | 16.3665 | 193.986 | 28.185 | 17.0392 | 13.9447 | 197.9531 | 30.9977 | 11.9596 | 13.773 | 195.9442 | 18.3867 | 45.0123 | 14.1156 | 196.1609 | 19.0069 | 45.0625 | 14.0615 | 197.7221 | 195.2215 | 13.3208 | 43.5389 | 5.7198 | 9.9698 | 0 | 77.4132 | 21.9424 | 48.4886 | 13.5698 | 191.5672 | 195.0821 | 13.2376 | 3.2195 | 46.1835 | 94.5533 | 140.7368 | 12.0291 | 134.4654 | 94.6228 | 14.605 | 6.7832 | 16.3665 | 193.986 | 88.3973 | 14.984 | 0.96117 | 0.24311 | 1.3811 | 92.8016 | 0.10561 | 0.20438 | 0.81241 | 0.083463 | 0.633 | 2.3607
2025-06-18 07:00 | 34.118 | 5.4642 | 0.75794 | 0.77152 | 16.2409 | 4.2746 | 12.7638 | 193.1864 | 16.3217 | 193.9611 | 27.7374 | 16.6672 | 13.8119 | 197.5375 | 31.0782 | 11.9793 | 13.6369 | 195.5747 | 18.3357 | 45.0313 | 13.9536 | 195.8602 | 18.9596 | 45.0709 | 13.9357 | 197.3764 | 194.787 | 13.1798 | 43.5361 | 5.3185 | 9.9732 | 0 | 77.5969 | 21.9677 | 49.1439 | 13.4459 | 191.4109 | 194.6291 | 13.094 | 3.3852 | 51.7892 | 94.0524 | 145.8415 | 12.0448 | 134.8732 | 95.2955 | 14.6079 | 6.7889 | 16.3217 | 193.9611 | 88.5325 | 14.93 | 0.91998 | 0.25661 | 1.3904 | 93.7009 | 0.10884 | 0.16387 | 0.81595 | 0.087404 | 0.61842 | 1.3768
2025-06-18 08:00 | 34.1475 | 5.673 | 0.80258 | 0.82112 | 18.3353 | 4.3563 | 12.7549 | 193.1779 | 16.2811 | 193.8904 | 28.3624 | 17.0285 | 13.8707 | 197.6152 | 31.1618 | 12.0015 | 13.6615 | 195.6272 | 18.3712 | 45.0416 | 13.9542 | 195.9704 | 18.9751 | 45.0885 | 13.9523 | 197.4749 | 194.8197 | 13.1885 | 44.1625 | 5.1706 | 9.9738 | 0 | 78.0073 | 22.009 | 49.3879 | 13.4605 | 191.5839 | 194.6223 | 13.0869 | 3.3605 | 56.2893 | 92.468 | 148.7573 | 12.0312 | 134.7649 | 95.2486 | 14.6118 | 6.8129 | 16.2811 | 193.8904 | 88.3823 | 14.8882 | 0.84869 | 0.25415 | 1.3916 | 93.7686 | 0.11311 | 0.12009 | 0.84129 | 0.091866 | 0.58641 | 1.1605
2025-06-18 09:00 | 34.042 | 5.154 | 0.82127 | 0.83508 | 19.057 | 4.4043 | 12.7206 | 193.03 | 16.3982 | 193.7215 | 28.069 | 17.5734 | 13.8579 | 197.4505 | 31.2396 | 12.0079 | 13.6413 | 195.5096 | 18.4019 | 45.0387 | 13.9468 | 195.9105 | 18.9923 | 45.1062 | 13.9233 | 197.3512 | 194.6619 | 13.1536 | 43.9449 | 5.03 | 9.9745 | 0 | 78.4418 | 22.0233 | 49.9348 | 13.4388 | 191.5042 | 194.4769 | 13.051 | 3.4894 | 56.0316 | 93.8985 | 149.9301 | 12.153 | 135.4055 | 94.9754 | 14.6138 | 6.8907 | 16.3982 | 193.7215 | 88.8388 | 14.9905 | 0.81473 | 0.21566 | 1.4064 | 93.5499 | 0.11555 | 0.11429 | 1.9364 | 0.094132 | 0.55831 | 1.0079
2025-06-18 10:00 | 33.9806 | 5.3859 | 0.84749 | 0.86128 | 19.546 | 4.2921 | 12.7406 | 193.0742 | 16.1738 | 193.742 | 28.4044 | 17.7215 | 13.906 | 197.5463 | 31.317 | 12.0085 | 13.6787 | 195.5874 | 18.4372 | 45.0363 | 13.9981 | 195.9669 | 18.9882 | 45.1127 | 13.9481 | 197.4017 | 194.7267 | 13.1841 | 44.2757 | 4.4422 | 9.9809 | 0 | 78.8267 | 22.0126 | 49.9989 | 13.4642 | 191.5464 | 194.5184 | 13.0695 | 3.526 | 53.6917 | 92.1553 | 145.847 | 11.9149 | 133.9966 | 95.8424 | 14.6135 | 6.7593 | 16.1738 | 193.742 | 89.2804 | 14.8187 | 0.81109 | 0.18252 | 1.3535 | 93.8997 | 0.11682 | 0.11549 | 1.1714 | 0.094767 | 0.53902 | 1.2238
2025-06-18 11:00 | 34.0192 | 5.213 | 0.83631 | 0.85063 | 19.0909 | 4.3191 | 12.7666 | 193.1743 | 16.2821 | 193.7815 | 28.3033 | 18.0707 | 13.9309 | 197.6019 | 31.3715 | 12.0068 | 13.6991 | 195.6696 | 18.438 | 45.0403 | 14.0235 | 196.0223 | 18.9846 | 45.0996 | 13.9625 | 197.4603 | 194.8042 | 13.2033 | 44.1198 | 3.7129 | 9.9824 | 0 | 79.0452 | 21.9907 | 49.937 | 13.4833 | 191.5872 | 194.6027 | 13.0938 | 3.387 | 52.1202 | 94.8132 | 146.9334 | 12.3609 | 136.0525 | 95.7957 | 14.6125 | 7.022 | 16.2821 | 193.7815 | 88.9515 | 14.9494 | 0.84033 | 0.18985 | 1.3309 | 94.4458 | 0.11535 | 0.11317 | 0.10425 | 0.092794 | 0.55018 | 1.0445
2025-06-18 12:00 | 33.9111 | 5.2403 | 0.81687 | 0.83009 | 18.6663 | 4.2934 | 12.7244 | 193.0491 | 16.0152 | 193.8427 | 27.7685 | 17.5982 | 13.8527 | 197.4289 | 31.3631 | 11.1365 | 13.6309 | 195.4842 | 18.3844 | 45.0455 | 13.9572 | 195.8738 | 18.9469 | 45.0883 | 13.9047 | 197.2874 | 194.6604 | 13.1505 | 43.7736 | 3.2244 | 9.9796 | 0 | 79.1666 | 21.98 | 49.9476 | 13.4376 | 191.4444 | 194.4871 | 13.052 | 3.2701 | 51.8553 | 93.7379 | 145.5933 | 12.2611 | 134.8821 | 95.1113 | 14.6122 | 6.965 | 16.0152 | 193.8427 | 88.4041 | 14.6891 | 0.87462 | 0.2062 | 1.3245 | 93.5411 | 0.11331 | 0.11076 | 0.10244 | 0.090829 | 0.57461 | 0.80253
2025-06-18 13:00 | 33.9757 | 6.8981 | 0.82608 | 0.84171 | 18.8078 | 4.2049 | 12.7343 | 193.0498 | 15.8896 | 193.704 | 28.3908 | 17.0868 | 13.8723 | 197.4898 | 31.3076 | 10.1865 | 13.6405 | 195.4296 | 18.4223 | 45.0443 | 13.9686 | 195.8887 | 18.9849 | 45.0891 | 13.9193 | 197.2831 | 194.6785 | 13.1664 | 44.0771 | 3.1211 | 9.98 | 0 | 79.2927 | 21.9804 | 50.0223 | 13.4473 | 191.3528 | 194.4989 | 13.0641 | 3.2818 | 50.8437 | 92.0207 | 142.8644 | 12.1155 | 133.618 | 95.5825 | 14.6123 | 6.8638 | 15.8896 | 193.704 | 88.8576 | 14.5632 | 0.88378 | 0.21501 | 1.3252 | 93.6893 | 0.11248 | 0.11034 | 0.49122 | 0.089692 | 0.58767 | 1.1169
2025-06-18 14:00 | 33.7409 | 7.3081 | 0.82299 | 0.83705 | 18.8796 | 4.2473 | 12.684 | 192.8876 | 16.086 | 193.5828 | 28.1472 | 17.0602 | 13.8047 | 197.2856 | 31.3146 | 10.1014 | 13.5786 | 195.2652 | 18.3673 | 45.0456 | 13.9069 | 195.7174 | 18.9672 | 45.0885 | 13.8638 | 197.1332 | 194.4927 | 13.1076 | 43.7296 | 3.307 | 9.9776 | 0 | 79.4131 | 21.9693 | 50.0899 | 13.3965 | 191.2172 | 194.3363 | 13.0148 | 3.1223 | 49.072 | 94.2366 | 143.3086 | 12.3221 | 135.176 | 95.6621 | 14.6129 | 6.9444 | 16.086 | 193.5828 | 88.5175 | 14.7307 | 0.89229 | 0.22751 | 1.3539 | 94.169 | 0.11224 | 0.10975 | 0.49088 | 0.088877 | 0.60219 | 0.98109
2025-06-18 15:00 | 33.8862 | 5.1308 | 0.82032 | 0.83532 | 18.8458 | 4.1736 | 12.6842 | 192.9036 | 15.8465 | 193.6088 | 28.4332 | 17.0531 | 13.8253 | 197.3417 | 31.3547 | 10.0929 | 13.5853 | 195.2867 | 18.3606 | 45.0493 | 13.913 | 195.7069 | 18.9358 | 45.0846 | 13.8669 | 197.1766 | 194.5246 | 13.1152 | 43.9699 | 3.6033 | 9.9764 | 0 | 79.5749 | 21.9708 | 50.1032 | 13.4025 | 191.2463 | 194.3561 | 13.0153 | 3.1859 | 49.2192 | 92.208 | 141.4271 | 12.0005 | 133.9587 | 95.2941 | 14.6143 | 6.7829 | 15.8465 | 193.6088 | 87.9423 | 14.5145 | 0.88541 | 0.224 | 1.3306 | 93.2131 | 0.1133 | 0.11004 | 0.074919 | 0.089435 | 0.59136 | 0.84916
2025-06-18 16:00 | 33.9193 | 4.0458 | 0.80784 | 0.82492 | 18.2906 | 4.1663 | 12.6931 | 192.8955 | 15.8424 | 193.5644 | 28.3507 | 17.0549 | 13.8435 | 197.3003 | 31.3704 | 10.0897 | 13.5931 | 195.2313 | 18.4123 | 45.0453 | 13.9316 | 195.6819 | 18.9536 | 45.0843 | 13.8669 | 197.1372 | 194.4953 | 13.1189 | 43.7109 | 3.7767 | 9.9779 | 0 | 79.7017 | 21.9645 | 50.1103 | 13.4065 | 191.1697 | 194.3413 | 13.0207 | 3.2877 | 47.6528 | 93.665 | 141.3179 | 12.0667 | 134.4518 | 95.1829 | 14.613 | 6.8268 | 15.8424 | 193.5644 | 88.7672 | 14.5032 | 0.89068 | 0.2142 | 1.3375 | 93.8408 | 0.11314 | 0.11064 | 0.29806 | 0.088996 | 0.59052 | 0.85326
2025-06-18 17:00 | 33.6121 | 6.239 | 0.8091 | 0.83635 | 17.7877 | 4.1909 | 12.6367 | 192.7283 | 15.8394 | 193.5528 | 28.0374 | 17.0811 | 13.7542 | 197.1366 | 31.3866 | 10.0966 | 13.5234 | 195.0874 | 18.3451 | 45.0367 | 13.8751 | 195.5133 | 18.9259 | 45.076 | 13.8049 | 196.9694 | 194.3365 | 13.0574 | 43.6748 | 3.6767 | 9.9737 | 0 | 79.7033 | 21.9284 | 50.1694 | 13.3357 | 191.0236 | 194.2013 | 12.9667 | 3.3667 | 47.9207 | 92.9446 | 140.8653 | 11.9405 | 133.7173 | 95.6254 | 14.6095 | 6.715 | 15.8394 | 193.5528 | 88.3785 | 14.4874 | 0.90887 | 0.21761 | 1.3499 | 94.2642 | 0.1102 | 0.11978 | 0.29535 | 0.086792 | 0.61763 | 0.67179
2025-06-18 18:00 | 33.7669 | 7.9104 | 0.82131 | 0.85633 | 17.3365 | 4.2109 | 12.648 | 192.7973 | 15.9071 | 193.4011 | 28.3782 | 17.5542 | 13.7466 | 197.2514 | 31.4129 | 10.1043 | 13.5293 | 195.1743 | 18.3398 | 45.0317 | 13.8914 | 195.5612 | 18.9325 | 45.0626 | 13.8225 | 197.0436 | 194.4216 | 13.0709 | 43.9492 | 3.5501 | 9.971 | 0 | 79.6062 | 21.903 | 50.1706 | 13.3349 | 191.0213 | 194.288 | 12.9817 | 3.4342 | 49.4961 | 92.6925 | 142.1887 | 12.007 | 133.7091 | 95.6461 | 14.607 | 6.7634 | 15.9071 | 193.4011 | 87.6908 | 14.5242 | 0.91701 | 0.21986 | 1.381 | 93.451 | 0.10748 | 0.14059 | 0.069549 | 0.084962 | 0.63566 | 0.62861
2025-06-18 19:00 | 33.6549 | 7.5372 | 0.82094 | 0.84652 | 16.6756 | 4.2643 | 12.6214 | 192.6618 | 16.0094 | 193.3609 | 27.9886 | 18.1304 | 13.6958 | 197.0664 | 31.4582 | 10.1135 | 13.489 | 195.0564 | 18.3046 | 45.0308 | 13.8557 | 195.3969 | 18.9157 | 45.0536 | 13.7872 | 196.8821 | 194.2489 | 13.0327 | 43.538 | 3.534 | 9.9725 | 0 | 79.4685 | 21.8878 | 50.1767 | 13.3028 | 190.8242 | 194.1334 | 12.9536 | 3.3295 | 48.4326 | 95.0822 | 143.5148 | 12.1945 | 134.7606 | 95.5094 | 14.6058 | 6.8601 | 16.0094 | 193.3609 | 87.8763 | 14.6043 | 0.92186 | 0.21872 | 1.4038 | 93.932 | 0.10642 | 0.16289 | 0.20928 | 0.08418 | 0.64622 | 0.60515
2025-06-18 20:00 | 33.6901 | 6.8652 | 0.82727 | 0.83903 | 16.1754 | 4.1932 | 12.6523 | 192.7952 | 15.8461 | 193.4978 | 28.3225 | 18.6263 | 13.734 | 197.2544 | 31.496 | 10.1213 | 13.5239 | 195.2049 | 18.2862 | 45.0302 | 13.8904 | 195.4874 | 18.8816 | 45.0481 | 13.82 | 197.0304 | 194.4106 | 13.072 | 43.9426 | 3.3471 | 9.9722 | 0 | 79.3147 | 21.8775 | 50.1704 | 13.3302 | 190.9291 | 194.2716 | 12.9856 | 3.3681 | 49.0628 | 92.2077 | 141.2705 | 11.8949 | 133.0503 | 96.0087 | 14.6054 | 6.6792 | 15.8461 | 193.4978 | 87.6341 | 14.446 | 0.92737 | 0.21576 | 1.3992 | 94.2263 | 0.10601 | 0.17611 | 0.20905 | 0.083887 | 0.65455 | 0.63811
2025-06-18 21:00 | 33.9819 | 5.4752 | 0.79147 | 0.79643 | 15.4744 | 4.1781 | 12.7542 | 193.1645 | 15.9691 | 193.5128 | 28.0968 | 18.9994 | 13.8182 | 197.5318 | 31.5327 | 10.1237 | 13.6124 | 195.4948 | 18.321 | 45.0297 | 13.9769 | 195.7426 | 18.8904 | 45.044 | 13.906 | 197.3094 | 194.7459 | 13.1669 | 43.4629 | 3.0366 | 9.9738 | 0 | 79.1726 | 21.8832 | 49.9496 | 13.4237 | 191.1841 | 194.6342 | 13.0841 | 3.5091 | 48.2645 | 93.7155 | 141.98 | 12.0235 | 133.7536 | 95.3274 | 14.6047 | 6.7638 | 15.9691 | 193.5128 | 87.3474 | 14.5272 | 0.93157 | 0.21472 | 1.4405 | 93.526 | 0.10586 | 0.18289 | 0.11495 | 0.08369 | 0.65501 | 0.91259
2025-06-18 22:00 | 34.0685 | 4.9852 | 0.7437 | 0.74928 | 15.5667 | 4.1507 | 12.795 | 193.2868 | 15.9246 | 193.6466 | 27.828 | 18.8258 | 13.8416 | 197.6151 | 31.5636 | 10.1192 | 13.6418 | 195.6167 | 18.3129 | 45.0285 | 14.0029 | 195.8339 | 18.8808 | 45.0441 | 13.9356 | 197.3831 | 194.8522 | 13.2032 | 43.2246 | 2.9773 | 9.9695 | 0 | 79.0721 | 21.8848 | 49.2733 | 13.4597 | 191.3365 | 194.7731 | 13.1228 | 3.2283 | 48.3238 | 93.0833 | 141.4071 | 11.8257 | 133.3938 | 95.5247 | 14.6046 | 6.6179 | 15.9246 | 193.6466 | 86.8092 | 14.458 | 0.92978 | 0.21576 | 1.4649 | 93.3538 | 0.10595 | 0.18371 | 0.11483 | 0.083681 | 0.64614 | 1.2593
2025-06-18 23:00 | 34.2675 | 4.7212 | 0.73924 | 0.74701 | 16.2127 | 4.128 | 12.7859 | 193.2586 | 15.9447 | 193.653 | 28.2774 | 18.3456 | 13.8539 | 197.6532 | 31.5934 | 10.1107 | 13.6458 | 195.6606 | 18.3679 | 45.0279 | 14.0073 | 195.8977 | 18.9144 | 45.0502 | 13.9424 | 197.4181 | 194.8463 | 13.2008 | 43.6263 | 3.212 | 9.967 | 0 | 79.0564 | 21.8969 | 49.0307 | 13.4542 | 191.4036 | 194.7425 | 13.1152 | 2.9539 | 48.4471 | 93.0097 | 141.4568 | 11.878 | 134.1441 | 95.5034 | 14.6051 | 6.6364 | 15.9447 | 193.653 | 86.7662 | 14.4677 | 0.92504 | 0.21822 | 1.4754 | 93.3082 | 0.1064 | 0.17692 | 0.33761 | 0.08415 | 0.63364 | 1.2924
2025-06-19 | 33.7884 | 3.3345 | 0.73943 | 0.74569 | 16.3471 | 4.2034 | 12.5052 | 192.2599 | 15.5599 | 194.5737 | 29.5261 | 18.0357 | 13.6627 | 196.9764 | 31.6228 | 10.104 | 13.4213 | 194.9861 | 18.2681 | 45.0321 | 13.7864 | 195.2965 | 18.8012 | 45.0569 | 13.7235 | 196.7342 | 193.9837 | 12.951 | 44.8934 | 3.4424 | 9.9699 | 0 | 79.0973 | 21.8723 | 50.1467 | 13.193 | 190.8574 | 193.7321 | 12.8409 | 3.1076 | 49.9263 | 92.0983 | 142.0247 | 11.8685 | 134.0164 | 97.1225 | 14.605 | 6.5735 | 15.5599 | 194.5737 | 85.5257 | 14.1073 | 0.91886 | 0.21915 | 1.4546 | 97.8359 | 0.10712 | 0.17144 | 0.083913 | 0.084647 | 0.62923 | 0.44553
Total | MW: 815.7743; MVAR: 126.6688; kg/s: 3785865.4298; kg/s: 290484.2697; kg/s: 4290758.1773; kg/s: 8060346.1953; kg/s: 12351104.3726; kg/s: 11595293.0121
Average | 33.9906 | 5.2779 | 0.79586 | 0.80755 | 16.84 | 4.2059 | 12.7349 | 193.0735 | 16.0819 | 193.7355 | 28.2014 | 17.6697 | 13.8313 | 197.475 | 31.2219 | 11.0115 | 13.6225 | 195.464 | 18.3582 | 45.029 | 13.9648 | 195.7895 | 18.9455 | 45.072 | 13.9086 | 197.2881 | 194.6829 | 13.1576 | 43.8179 | 4.2946 | 9.9734 | 0 | 78.7193 | 21.9389 | 49.7185 | 13.4239 | 191.2794 | 194.5306 | 13.0652 | 3.3621 | 49.6616 | 93.291 | 142.9526 | 12.0517 | 134.2048 | 95.4446 | 14.6083 | 6.805 | 16.0819 | 193.7355 | 88.1378 | 14.7059 | 0.91117 | 0.22284 | 1.3746 | 93.7918 | 0.1092 | 0.15509 | 0.53243 | 0.086863 | 0.61502 | 1.1259
Min | 33.6121 | 3.0717 | 0.72386 | 0.73214 | 13.73 | 3.9926 | 12.5052 | 192.2599 | 15.5599 | 193.3609 | 27.7374 | 16.6672 | 13.6627 | 196.9764 | 30.4151 | 10.0897 | 13.4213 | 194.9861 | 18.2681 | 45.0027 | 13.7864 | 195.2965 | 18.8012 | 45.044 | 13.7235 | 196.7342 | 193.9837 | 12.951 | 43.2246 | 2.9773 | 9.967 | 0 | 77.4132 | 21.8723 | 48.1163 | 13.193 | 190.8242 | 193.7321 | 12.8409 | 2.9539 | 45.6446 | 91.7559 | 137.4005 | 11.7381 | 132.5243 | 94.6228 | 14.6041 | 6.5735 | 15.5599 | 193.3609 | 85.5257 | 14.1073 | 0.81109 | 0.18252 | 1.3108 | 92.4709 | 0.10483 | 0.10975 | 0.069549 | 0.082811 | 0.53902 | 0.44553
Max | 34.4719 | 7.9104 | 0.84749 | 0.86128 | 19.546 | 4.4043 | 12.9282 | 193.7634 | 16.4163 | 194.5737 | 29.5261 | 18.9994 | 13.9702 | 198.0575 | 31.6228 | 12.0085 | 13.7918 | 196.0106 | 18.438 | 45.0493 | 14.141 | 196.2214 | 19.0069 | 45.1127 | 14.0754 | 197.8252 | 195.3379 | 13.3422 | 44.8934 | 6.0344 | 9.9824 | 0 | 79.7033 | 22.0233 | 50.1767 | 13.5845 | 191.6635 | 195.2108 | 13.255 | 3.8325 | 56.2893 | 95.0822 | 149.9301 | 12.3609 | 136.0525 | 97.1225 | 14.6143 | 7.0278 | 16.4163 | 194.5737 | 89.2804 | 15.0799 | 0.97613 | 0.25661 | 1.4754 | 97.8359 | 0.11682 | 0.21225 | 1.9364 | 0.094767 | 0.65501 | 2.4407

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1
18 |  | Night | 22:15 | 5.55 | 22.2
19 | 2025-06-10 | Day | 8:55 | 5.69 | 31.6
20 |  | Night | 0:20 | 5.18 | 24.3
21 | 2025-06-11 | Day | 17:00 | 5.07 | 21.6
22 |  | Night | 22:30 | 5.62 | 28.8
23 | 2025-06-12 | Day | 10:10 | 5.08 | 27.3
24 |  | Night | 21:30 | 5.64 | 26.6
25 | 2025-06-13 | Day | 8:40 | 5.11 | 27.1
26 |  | Night | 22:00 | 5.77 | 25.5
27 | 2025-06-14 | Day | 10:00 | 5.55 | 32
28 |  | Night | 22:00 | 5.78 | 28.9
29 | 2025-06-15 | Day | 10:00 | 5.33 | 24.6
30 |  | Night | 23:45 | 5.82 | 30.3
31 | 2025-06-16 | Day | 9:40 | 5.44 | 27.9
32 |  | Night | 23:45 | 5.97 | 23.8
33 | 2025-06-17 | Day | 15:30 | 5.77 | 33
34 |  | Night | 22:45 | 5.86 | 27.7
35 | 2025-06-18 | Day | 10:35 | 5 | 21
36 |  | Night | 23:30 | 5.97 | 21.6
37 | 2025-06-19 | Day
38 |  | Night
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-18
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0