## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-19
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 27.4956 | 197.8997 | 21.3052
|  | #6-2 | Production | 31.8886 | 195.7699 | 10.9473
|  | #6-3 | Production | 18.3952 | 196.0978 | 45.0246
|  | #6-4 | Production | 18.7926 | 197.4782 | 45.6731
|  | #8-1 | Shut in | 2.978 | 80.7615 | 9.9749
|  | #8-2 | Production | 21.858 | 191.5209 | 50.7853
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 43.6897 | 3774793.4562
|  | PAD #8 - STEAM |  |  |  |  | 3.3995 | 293720.8142 | Online
|  | BRINE HEADER |  |  |  |  | 102.0125 | 8813875.7021 | Offline
|  | TOTAL FLOW |  |  |  |  | 149.1017 | 12882389.9725
|  | PRESS SEPARATOR IJN 6 | Online | 13.1952 | 194.8081
|  | PRESS SEPARATOR IJN 8 | Online | 13.1026 | 194.6693
| INJECTION WELL | #5-1 | Injection | 7.7377 | 96.3792 | 16.953 | 141.2324 | 12202479.1963
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.5003 |  |  | 828.0072
|  | NET | 31.8092 |  |  | 763.4217
| PARASITIC LOAD |  | 2.6911 |  |  | 64.5855
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 4.3218 |  |  | 15558.3066
|  | NET | 4.6874 |  |  | 16874.5405
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 6. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
7. Brine Dump Control valve Ijen-6 PV-2227A indication passing
8. Compressor A have indication noise on bearing screw pump

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-19
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 763421.6758 |  | 0 |  | 763421.6758
|  |  |  | 763421.6758 |  | 0 |  | 763421.6758
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 766160 | [7 empty] | 766160
M-T-D GROSS GENERATION (kWHR) |  |  |  | 15685064 | [7 empty] | 15685064
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18713.88 | 27681.32 | 4270.04 | 44.1 | 928 | 777 | 24733.02
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 348661.13 | 3133037.86 | 96940.79 | 827.1 | 21657 | 24667 | 144091.89
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.5003 |  |  | 4.9404 |  | 17.5525
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 456
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 92.21%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 3774.7935 |  | 293.7208 |  |  | 4297.9893
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.04369 |  | 0.0033995 |  |  | 0.049745
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 8813.8757
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.10201
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 13111.865
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.15176
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 193.2085 |  |  |  | 193.9814
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.7736 |  |  |  | 16.3595
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 15.4056 |  | 20.4579 |  |  | 17.5525
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
6. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
7. Brine Dump Control valve Ijen-6 PV-2227A indication passing
8. Compressor A have indication noise on bearing screw pump
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
5:51 | Open drain suction strainer of Reinjection Pump-B due to prepare cleaning
6:59 | Running test diesel pit pump IJN-6 --> Level fuel : 107 cm, level pond : 26.3%, Speed : 1483 Rpm, Discharge Pressure : 18 Bar --> Result : seal oil leakage little bit
7:06 | Stop running test diesel pit pump IJN-6 --> Level pond : 26%
8:15 | Daily tool box meeting
9:00 | Weekly housekeeping Power block area
9:51 | Continue troubleshoot streetlighting (by MTC team)
10:06 | Pull out strainer Re-injection pump B due to cleaning by MTC team
10:11 | Turn on air dryer B until dew point more than -40.0 degC for prepare switching schedule
10:31 | Switching air dryer A to B (Dew point air dryer B -41.1 degC)
11:10 | Swipe strainer B to A Brine Booster Pump IJN 8 due to high delta pressure more than 0.6 barg
11:30 | Filling service water tank from baker tank (Level SW tank before filling : 40.8% , after filling : 47.2%)
14:25 | Check and Release Pressure & Condensate Master Valve & Wing Valve PW IJN 5-1 (Standart activities schedule)
14:30 | Fire Extinguisher Inspection (Standart activities schedule)
14:36 | Flammable Gas Detector Inspection (Standart activities schedule)
14:50 | Hose box inpection (Standart activities schedule)
15:37 | Rectify sand filter panel due to cannot run if auto mode
16:30 | Brine bypass control valve A (PV-2503) offline exercise and switch priority from B to A (Standart activities schedule)
16:40 | Rock Muffler control valve A (PV2430) offline exercise switch priority from B to A (Standart activities schedule)
19:45 | Handover day shift to night shift
IX.) SERVICE REQUEST
SR-06-2025-0011 | Differential pressure strainer-B of brine booster pump IJN-8 reach 0.62 Bar
SR-06-2025-0012 | Different reading around 3 Bars for PT-2006A and PG (PI-2007A) on wellhead pressure 6-1
SR-06-2025-0013 | Different reading around 6 Bars for PT-2106A and PG (PI-2107A) on wellhead pressure 8-1
SR-06-2025-0014 | Different reading around 3 Bars for PT-2006C and PG (PI-2007C) on wellhead pressure 6-3
SR-06-2025-0015 | Different reading around 3 Bars for PT-2006B and PG (PI-2007B) on wellhead pressure 6-2
SR-06-2025-0016 | Door housing station FM-200 cannot open
X.) SHIFT CREW
Day Shift | Shift Leader : Hary |  |  |  | CCR Operator : Ois |  |  |  | Steamfield : Dadan
Night Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Fauzan |  |  |  | Steamfield : Vandy

## Meter
DATE: | 2025-06-19
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2245040 | 2255840 | 10800 | 127990
(BACKUP) |  | 2126290 | 2243340 | 2254120 | 10780 | 127830
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 106766870 | 107533030 | 766160 | 14431120
(BACKUP) |  | 93082960 | 106744040 | 107509990 | 765950 | 14427030
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4728350 | 4746040 | 17690 | 603810
(BACKUP) |  | 4144060 | 4730360 | 4748060 | 17700 | 604000
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 116176041 | 117008319 | 832278 | 15685064
TOTAL |  |  |  |  | 832278 | 15685064
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 19020822 | 19138991 | 118169 | 2608736
TOTAL |  |  |  |  | 118169 | 2608736
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3419265.59 | 3437979.47 | 18713.88 | 348661.13
U3B |  | 283254.3 | 3388610.84 | 3416292.16 | 27681.32 | 3133037.86
U3C |  | 989758.41 | 1082429.16 | 1086699.2 | 4270.04 | 96940.79
U Ijen 5 |  | 7258.6 | 8041.6 | 8085.7 | 44.1 | 827.1
U Ijen 6 |  | 247889 | 268618 | 269546 | 928 | 21657
U Ijen 8 |  | 299837 | 323727 | 324504 | 777 | 24667
TOTAL |  |  |  |  | 52414.34 | 492753.02
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power meter already reading on 17 June 2025 - Initial value following U3A on 3 Millions
Note on G43: Operator MPGS: - Power meter already reading on 17 June 2025 - Initial value following U3A on 3 Millions

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater |  | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Delta Pressure | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | oC | Bara | % | % | Barg | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | TT-2601 | PT-2603 | PV-2503A | PV-2503B | PV-2503 | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-19 01:00 | 34.1592 | 2.5561 | 0.74522 | 0.75268 | 16.2347 | 4.1224 | 12.7629 | 193.1699 | 15.8511 | 193.7106 | 28.2932 | 18.0351 | 13.8409 | 197.5777 | 31.6462 | 10.1057 | 13.6246 | 195.6497 | 18.3277 | 45.0266 | 13.9818 | 195.8456 | 18.9 | 45.0545 | 13.9229 | 197.3656 | 194.7668 | 13.1802 | 43.6887 | 3.5282 | 9.9685 | 0 | 79.1512 | 21.9033 | 49.4503 | 13.4364 | 191.3719 | 194.6378 | 13.0923 | 3.1725 | 49.0922 | 91.7273 | 140.8195 | 11.6896 | 133.1002 | 95.8233 | 14.606 | 6.5054 | 87.2074 | 14.3905 | 0.91001 | 0.22182 | 1.4589 | 93.6381 | 0.107 | 0.16489 | 0.51726 | 0.084854 | 0.62455 | 1.1419
2025-06-19 02:00 | 34.1604 | 2.5448 | 0.75066 | 0.75838 | 16.4156 | 4.1875 | 12.7924 | 193.2871 | 16.0186 | 193.7276 | 28.1145 | 18.0321 | 13.8626 | 197.6406 | 31.6904 | 10.1047 | 13.6486 | 195.7444 | 18.3651 | 45.0265 | 14.0073 | 195.9336 | 18.9131 | 45.055 | 13.946 | 197.4517 | 194.8634 | 13.2048 | 43.3813 | 3.5495 | 9.9676 | 0 | 79.2219 | 21.9067 | 49.6716 | 13.4649 | 191.4742 | 194.7386 | 13.1201 | 3.3791 | 48.8095 | 94.2382 | 143.0478 | 11.9731 | 134.6016 | 95.1287 | 14.6061 | 6.6644 | 87.1188 | 14.5321 | 0.90739 | 0.2198 | 1.4848 | 93.3174 | 0.10702 | 0.16324 | 0.068943 | 0.084962 | 0.62394 | 1.0545
2025-06-19 03:00 | 34.1573 | 3.1694 | 0.75395 | 0.76169 | 16.3077 | 4.1259 | 12.7801 | 193.2344 | 15.9564 | 193.813 | 28.0756 | 18.0315 | 13.8488 | 197.5995 | 31.7279 | 10.1058 | 13.636 | 195.6893 | 18.3418 | 45.0256 | 13.9953 | 195.8814 | 18.904 | 45.0533 | 13.9329 | 197.403 | 194.8173 | 13.1934 | 43.4536 | 3.4747 | 9.9677 | 0 | 79.2812 | 21.9051 | 49.7144 | 13.4527 | 191.4125 | 194.69 | 13.1079 | 3.4861 | 47.8059 | 93.123 | 140.9288 | 11.8045 | 133.8753 | 95.4197 | 14.6061 | 6.5635 | 86.8266 | 14.4681 | 0.9073 | 0.22014 | 1.487 | 93.3134 | 0.10691 | 0.16362 | 0.06878 | 0.084751 | 0.63029 | 1.0671
2025-06-19 04:00 | 34.1818 | 5.1483 | 0.75506 | 0.76175 | 16.2216 | 4.1342 | 12.7486 | 193.1254 | 15.9338 | 193.7971 | 28.3038 | 18.0344 | 13.8285 | 197.5393 | 31.7562 | 10.1081 | 13.6131 | 195.5955 | 18.3609 | 45.0244 | 13.975 | 195.8303 | 18.9156 | 45.0515 | 13.912 | 197.3414 | 194.7236 | 13.1656 | 43.7483 | 3.293 | 9.9686 | 0 | 79.3311 | 21.9026 | 49.582 | 13.4222 | 191.3352 | 194.5829 | 13.0781 | 3.4438 | 48.4606 | 92.8546 | 141.3152 | 11.8178 | 134.0483 | 95.9228 | 14.6057 | 6.5775 | 86.936 | 14.4069 | 0.90688 | 0.21993 | 1.5256 | 93.7903 | 0.1068 | 0.16276 | 0.29826 | 0.084433 | 0.63453 | 1.1108
2025-06-19 05:00 | 33.9544 | 5.9354 | 0.74931 | 0.75637 | 15.9001 | 4.2263 | 12.7759 | 193.1987 | 16.1051 | 193.6825 | 27.7938 | 18.0348 | 13.835 | 197.5132 | 31.7813 | 10.1077 | 13.6259 | 195.5695 | 18.3421 | 45.0241 | 13.9844 | 195.8327 | 18.917 | 45.0498 | 13.922 | 197.3348 | 194.7531 | 13.1814 | 43.1425 | 3.1103 | 9.9682 | 0 | 79.3697 | 21.9056 | 49.7581 | 13.4465 | 191.3274 | 194.6391 | 13.103 | 3.7143 | 48.1177 | 95.3838 | 143.5016 | 11.9805 | 134.8713 | 94.9595 | 14.6052 | 6.6538 | 87.1001 | 14.5523 | 0.90833 | 0.22169 | 1.5512 | 93.4833 | 0.10664 | 0.16468 | 0.36641 | 0.084365 | 0.63228 | 1.2169
2025-06-19 06:00 | 34.0729 | 5.8464 | 0.75681 | 0.76592 | 16.3241 | 4.1628 | 12.8049 | 193.3102 | 15.9618 | 193.7823 | 28.2891 | 18.0348 | 13.8749 | 197.6944 | 31.8001 | 10.1016 | 13.6616 | 195.7008 | 18.3263 | 45.0268 | 14.0057 | 195.93 | 18.868 | 45.1807 | 13.9554 | 197.4157 | 194.8961 | 13.2196 | 43.5575 | 3.1478 | 9.9695 | 0 | 79.4162 | 21.911 | 49.499 | 13.4796 | 191.4722 | 194.7573 | 13.1333 | 3.5972 | 49.0485 | 92.7911 | 141.8396 | 11.7408 | 133.5514 | 95.7206 | 14.6061 | 6.5228 | 86.7113 | 14.413 | 0.89961 | 0.22882 | 1.5469 | 93.5437 | 0.10716 | 0.15601 | 0.13723 | 0.085056 | 0.62734 | 1.2428
2025-06-19 07:00 | 34.1189 | 5.8141 | 0.77564 | 0.78923 | 17.6871 | 4.219 | 12.7768 | 193.2305 | 16.1807 | 193.7363 | 28.102 | 18.0415 | 13.865 | 197.6258 | 31.8276 | 10.0901 | 13.6471 | 195.668 | 18.376 | 45.0322 | 13.9756 | 195.9662 | 18.9199 | 45.6913 | 13.9529 | 197.3555 | 194.8215 | 13.1941 | 43.6068 | 3.3564 | 9.9722 | 0 | 79.6034 | 21.9414 | 49.5058 | 13.4659 | 191.5017 | 194.6722 | 13.1061 | 3.2833 | 48.5827 | 95.3661 | 143.9488 | 12.1352 | 135.9912 | 95.6114 | 14.609 | 6.7587 | 86.7829 | 14.5869 | 0.87537 | 0.22881 | 1.5919 | 93.7972 | 0.10938 | 0.12977 | 0.44904 | 0.087614 | 0.61294 | 1.0782
2025-06-19 08:00 | 34.1315 | 6.0415 | 0.80264 | 0.82045 | 18.7084 | 4.1989 | 12.7304 | 193.0676 | 16.0968 | 193.6366 | 27.8993 | 18.5933 | 13.8602 | 197.52 | 31.8562 | 10.0712 | 13.6262 | 195.567 | 18.3642 | 45.0314 | 13.938 | 195.9452 | 18.9361 | 46.0768 | 13.9364 | 197.3417 | 194.6942 | 13.1608 | 44.0467 | 3.5002 | 9.978 | 0 | 79.9617 | 21.974 | 49.5725 | 13.4414 | 191.4983 | 194.5448 | 13.0622 | 3.2876 | 49.505 | 93.8093 | 143.3143 | 12.0231 | 135.4594 | 95.6331 | 14.6134 | 6.712 | 86.9422 | 14.5259 | 0.83167 | 0.22574 | 1.5692 | 93.7286 | 0.11273 | 0.11357 | 0.45277 | 0.091309 | 0.58898 | 1.1933
2025-06-19 09:00 | 34.1134 | 7.192 | 0.83114 | 0.84894 | 19.5162 | 4.303 | 12.7211 | 193.0322 | 16.3134 | 193.6876 | 27.2538 | 21.8573 | 13.9296 | 197.6671 | 31.8814 | 10.0577 | 13.6555 | 195.6154 | 18.3903 | 45.0248 | 13.9671 | 196.0304 | 18.7825 | 46.0905 | 13.9513 | 197.4278 | 194.6795 | 13.1614 | 44.3296 | 3.4857 | 9.9834 | 0 | 80.3871 | 21.9889 | 49.3536 | 13.4438 | 191.5646 | 194.5264 | 13.0529 | 3.6288 | 51.6563 | 95.1325 | 146.7888 | 12.316 | 136.8253 | 96.2418 | 14.6167 | 6.9063 | 86.9585 | 14.7022 | 0.78407 | 0.20244 | 1.6097 | 94.2826 | 0.11539 | 0.1145 | 1.7128 | 0.093563 | 0.56046 | 1.3062
2025-06-19 10:00 | 33.8772 | 7.0321 | 0.85513 | 0.87232 | 20.2145 | 4.5214 | 12.6374 | 192.7377 | 17.0035 | 193.67 | 25.4794 | 25.2058 | 13.8961 | 197.4907 | 31.9142 | 10.0586 | 13.5941 | 195.3704 | 18.4427 | 45.0198 | 13.9196 | 195.8751 | 18.6972 | 46.1007 | 13.8821 | 197.1279 | 194.3161 | 13.0581 | 43.4038 | 3.3357 | 9.9837 | 0 | 80.7889 | 21.9935 | 50.2443 | 13.3679 | 191.3096 | 194.1772 | 12.9654 | 3.588 | 51.4979 | 101.6737 | 153.1716 | 13.1403 | 140.7139 | 95.7863 | 14.6186 | 7.4407 | 87.484 | 15.3096 | 0.75746 | 0.17422 | 1.6925 | 94.3129 | 0.11679 | 0.11629 | 10.2442 | 0.094154 | 0.52388 | 0.83968
2025-06-19 11:00 | 34.0691 | 5.4061 | 0.87465 | 0.89291 | 20.4579 | 4.5399 | 12.5734 | 192.5009 | 17.2647 | 193.6905 | 25.2456 | 27.5104 | 13.9124 | 197.5352 | 31.9402 | 10.0604 | 13.5717 | 195.2603 | 18.4283 | 45.0182 | 13.9021 | 195.7928 | 18.7185 | 46.1064 | 13.8526 | 197.0164 | 194.0947 | 12.9971 | 43.6389 | 3.0389 | 9.987 | 0 | 81.1152 | 21.9758 | 52.1603 | 13.3177 | 191.1302 | 193.9331 | 12.9047 | 3.2413 | 52.8642 | 101.8068 | 154.671 | 13.3489 | 141.2544 | 96.1712 | 14.6195 | 7.6449 | 87.6469 | 15.5426 | 0.74605 | 0.1688 | 1.7206 | 94.5007 | 0.11792 | 0.11735 | 18.6758 | 0.094088 | 0.49537 | 0.40077
2025-06-19 12:00 | 34.5769 | 4.8049 | 0.87721 | 0.89711 | 20.0907 | 4.4656 | 12.7108 | 192.9846 | 17.4487 | 194.0589 | 26.0296 | 29.6277 | 14.1475 | 198.2893 | 31.9518 | 10.0578 | 13.7493 | 195.8252 | 18.3875 | 45.0197 | 14.0617 | 196.2358 | 18.7036 | 46.1072 | 14.0132 | 197.58 | 194.6332 | 13.1545 | 44.3992 | 2.8114 | 9.9906 | 0 | 81.3709 | 21.929 | 52.7657 | 13.4522 | 191.5169 | 194.4338 | 13.0435 | 3.3365 | 53.3984 | 101.0084 | 154.4068 | 13.4713 | 141.5612 | 96.2705 | 14.6199 | 7.7403 | 87.02 | 15.6949 | 0.75034 | 0.16879 | 1.7522 | 94.398 | 0.11858 | 0.11811 | 18.6963 | 0.093801 | 0.49477 | 0.54779
2025-06-19 13:00 | 34.9346 | 5.764 | 0.87425 | 0.89388 | 19.7266 | 4.5802 | 12.9276 | 193.7251 | 17.2383 | 194.5881 | 26.577 | 28.8604 | 14.3685 | 198.9685 | 31.958 | 10.4868 | 13.9545 | 196.4758 | 18.4499 | 45.0217 | 14.2503 | 196.7903 | 18.6983 | 46.1061 | 14.2041 | 198.1692 | 195.3532 | 13.3682 | 44.2035 | 2.8482 | 9.9911 | 0 | 81.585 | 21.8984 | 50.6455 | 13.6514 | 192.0874 | 195.1556 | 13.2522 | 3.3816 | 52.1519 | 107.8539 | 160.0057 | 12.9302 | 146.4666 | 95.7933 | 17.4095 | 8.3099 | 87.1004 | 15.3427 | 0.75952 | 0.16448 | 1.894 | 94.2628 | 0.11869 | 0.11792 | 10.5641 | 0.093889 | 0.50123 | 1.868
2025-06-19 14:00 | 35.0376 | 5.6915 | 0.86556 | 0.88408 | 19.3901 | 4.7152 | 12.9662 | 193.8445 | 16.5849 | 194.6316 | 26.8568 | 25.3948 | 14.321 | 198.8324 | 31.9608 | 11.4655 | 13.9501 | 196.4801 | 18.5389 | 45.0259 | 14.2633 | 196.8129 | 18.7551 | 46.0981 | 14.2067 | 198.104 | 195.4312 | 13.3927 | 43.56 | 3.0265 | 9.9861 | 0 | 81.7403 | 21.8984 | 49.4477 | 13.6805 | 192.1647 | 195.2758 | 13.2886 | 3.4657 | 51.399 | 113.8111 | 165.21 | 11.8655 | 150.5078 | 95.8962 | 21.0836 | 8.8579 | 87.1228 | 14.5867 | 0.78846 | 0.16983 | 1.9965 | 94.3198 | 0.11747 | 0.11597 | 2.0112 | 0.093385 | 0.52385 | 1.9402
2025-06-19 15:00 | 35.0247 | 4.5738 | 0.84847 | 0.86544 | 18.8901 | 4.6603 | 12.914 | 193.6751 | 16.3548 | 194.4543 | 27.0907 | 22.9651 | 14.2149 | 198.5081 | 31.9674 | 12.0076 | 13.8704 | 196.2573 | 18.5321 | 45.0289 | 14.2081 | 196.5988 | 18.7998 | 46.0863 | 14.1367 | 197.8845 | 195.2533 | 13.3379 | 43.326 | 3.0784 | 9.9791 | 0 | 81.8438 | 21.888 | 50.4092 | 13.6258 | 191.9944 | 195.1225 | 13.2383 | 3.526 | 51.2041 | 112.0204 | 163.2245 | 11.7008 | 148.7348 | 96.059 | 20.7683 | 8.8117 | 86.9377 | 14.3836 | 0.83259 | 0.1859 | 1.9696 | 94.1395 | 0.11571 | 0.11342 | 0.078159 | 0.091928 | 0.54892 | 1.062
2025-06-19 16:00 | 34.9896 | 3.3406 | 0.82016 | 0.83479 | 18.1281 | 4.5834 | 12.9339 | 193.7227 | 16.4256 | 194.5205 | 27.2521 | 22.4645 | 14.2122 | 198.5337 | 31.9607 | 11.9922 | 13.8734 | 196.2767 | 18.4679 | 45.0286 | 14.2197 | 196.5809 | 18.767 | 46.0704 | 14.1436 | 197.9218 | 195.296 | 13.3544 | 43.3203 | 2.9051 | 9.9754 | 0 | 81.8606 | 21.8446 | 50.4135 | 13.6259 | 191.9703 | 195.162 | 13.2567 | 3.1632 | 49.218 | 111.1543 | 160.3724 | 12.0742 | 147.5525 | 96.2615 | 19.3443 | 8.7531 | 87.1694 | 14.465 | 0.93825 | 0.19879 | 1.959 | 94.7475 | 0.11269 | 0.11198 | 0.07501 | 0.089335 | 0.95048 | 1.0797
2025-06-19 17:00 | 34.9208 | 4.0826 | 0.78867 | 0.80385 | 17.4336 | 4.5298 | 12.9301 | 193.7322 | 16.3815 | 194.4171 | 27.4334 | 21.4794 | 14.1493 | 198.4659 | 31.9515 | 11.983 | 13.8455 | 196.2605 | 18.4495 | 45.0279 | 14.1969 | 196.5684 | 18.7338 | 46.049 | 14.1273 | 197.8852 | 195.2964 | 13.3433 | 43.2911 | 2.7026 | 9.9712 | 0 | 81.7888 | 21.8039 | 50.007 | 13.6014 | 191.9665 | 195.1928 | 13.2551 | 2.7142 | 48.2113 | 109.973 | 158.1843 | 12.0348 | 146.729 | 96.4789 | 19.1194 | 8.6684 | 86.9856 | 14.4288 | 1.0542 | 0.20605 | 1.9514 | 94.7054 | 0.10933 | 0.11562 | 0.071718 | 0.087049 | 1.5293 | 0.63947
2025-06-19 18:00 | 34.8222 | 4.98 | 0.78436 | 0.79832 | 17.2207 | 4.5001 | 12.9105 | 193.6656 | 16.2991 | 194.237 | 27.6451 | 20.4679 | 14.0891 | 198.3103 | 31.9537 | 11.9814 | 13.8118 | 196.1475 | 18.476 | 45.0269 | 14.1719 | 196.5223 | 18.7625 | 46.0438 | 14.1003 | 197.7934 | 195.2267 | 13.321 | 43.2327 | 2.6949 | 9.9708 | 0 | 81.7372 | 21.7813 | 50.8994 | 13.5759 | 191.8803 | 195.1278 | 13.2366 | 3.0377 | 48.5378 | 108.1643 | 156.7021 | 11.8557 | 145.4748 | 96.2102 | 19.1183 | 8.5485 | 87.2009 | 14.3606 | 1.0853 | 0.20695 | 1.9369 | 94.5782 | 0.10829 | 0.12607 | 0.070791 | 0.086418 | 1.5858 | 0.4017
2025-06-19 19:00 | 34.7191 | 4.6308 | 0.78695 | 0.79162 | 16.9617 | 4.4918 | 12.8401 | 193.4256 | 16.1821 | 194.1623 | 27.7601 | 20.1186 | 14.01 | 198.0725 | 31.9543 | 11.9746 | 13.7402 | 195.9159 | 18.4127 | 45.026 | 14.1054 | 196.3329 | 18.7528 | 46.0529 | 14.0341 | 197.603 | 195.0004 | 13.2529 | 43.3052 | 2.8139 | 9.9707 | 0 | 81.7007 | 21.7526 | 51.6753 | 13.5052 | 191.6801 | 194.885 | 13.168 | 3.396 | 48.8172 | 107.1358 | 155.953 | 11.7922 | 144.8097 | 96.9109 | 19.1181 | 8.519 | 87.3686 | 14.2435 | 1.0922 | 0.20805 | 1.9367 | 95.2194 | 0.10769 | 0.13727 | 0.070118 | 0.085878 | 1.3659 | 0.4006
2025-06-19 20:00 | 34.6191 | 4.5817 | 0.81161 | 0.81629 | 16.6503 | 4.4884 | 12.7483 | 193.146 | 16.182 | 193.9456 | 27.794 | 20.1133 | 13.9238 | 197.8425 | 31.9595 | 11.9664 | 13.655 | 195.6862 | 18.3827 | 45.0241 | 14.0275 | 196.1068 | 18.7126 | 46.0526 | 13.9544 | 197.388 | 194.7428 | 13.1647 | 43.5908 | 2.8367 | 9.9691 | 0 | 81.6301 | 21.7308 | 52.1492 | 13.417 | 191.4171 | 194.6304 | 13.0793 | 3.5681 | 48.9507 | 106.4327 | 155.3834 | 11.7853 | 144.3897 | 97.2198 | 19.1173 | 8.526 | 87.1298 | 14.2316 | 1.0958 | 0.20793 | 1.9485 | 94.968 | 0.10705 | 0.15031 | 0.069418 | 0.085134 | 1.2054 | 0.39959
2025-06-19 21:00 | 34.713 | 4.3375 | 0.82084 | 0.83071 | 16.222 | 4.432 | 12.6982 | 192.9543 | 16.1358 | 193.786 | 27.8238 | 20.1064 | 13.8752 | 197.6849 | 31.9639 | 11.9653 | 13.6073 | 195.5163 | 18.4012 | 45.0223 | 13.9869 | 195.9194 | 18.7174 | 45.6905 | 13.9065 | 197.2445 | 194.562 | 13.1167 | 43.8103 | 2.6588 | 9.9688 | 0 | 81.5149 | 21.718 | 52.8445 | 13.3692 | 191.167 | 194.4341 | 13.0309 | 3.6764 | 48.6878 | 105.1616 | 153.8494 | 11.6699 | 143.2874 | 96.8179 | 19.1159 | 8.4554 | 86.9071 | 14.2115 | 1.0987 | 0.20575 | 1.9227 | 94.8978 | 0.1065 | 0.16333 | 0.068818 | 0.084446 | 1.1108 | 0.39715
2025-06-19 22:00 | 34.8705 | 4.9945 | 0.77566 | 0.78269 | 15.6605 | 4.3557 | 12.6654 | 192.8535 | 16.0999 | 193.7752 | 27.8792 | 20.1114 | 13.8344 | 197.5779 | 31.9703 | 11.9653 | 13.5668 | 195.4178 | 18.3273 | 45.0208 | 13.9464 | 195.7371 | 18.6924 | 45.1923 | 13.8625 | 197.141 | 194.4536 | 13.0812 | 43.7192 | 2.3038 | 9.9692 | 0 | 81.3836 | 21.7085 | 53.0777 | 13.3405 | 191.0628 | 194.3272 | 12.9994 | 3.5124 | 47.2701 | 104.6149 | 151.885 | 11.5568 | 142.8964 | 97.0876 | 19.1151 | 8.3645 | 86.7257 | 14.1826 | 1.0985 | 0.20407 | 1.9156 | 94.9584 | 0.10615 | 0.17265 | 0.068361 | 0.083953 | 1.0104 | 0.39534
2025-06-19 23:00 | 34.9868 | 5.053 | 0.75436 | 0.76 | 15.4913 | 4.3101 | 12.704 | 192.997 | 16.1468 | 193.7743 | 28.0802 | 20.109 | 13.8694 | 197.705 | 31.9779 | 11.96 | 13.6015 | 195.5508 | 18.3078 | 45.019 | 13.9801 | 195.7717 | 18.7323 | 45.0484 | 13.8969 | 197.2266 | 194.5878 | 13.119 | 43.6879 | 2.0572 | 9.9706 | 0 | 81.277 | 21.6873 | 53.0358 | 13.3784 | 191.1327 | 194.4617 | 13.0381 | 3.6039 | 46.4436 | 104.3521 | 150.7957 | 11.4976 | 142.7631 | 96.6507 | 19.1148 | 8.3141 | 87.1975 | 14.2118 | 1.0955 | 0.203 | 1.9331 | 94.6919 | 0.10596 | 0.18088 | 0.068087 | 0.08375 | 0.9248 | 0.39512
2025-06-20 | 34.796 | 5.0487 | 0.75413 | 0.75947 | 15.4056 | 4.6806 | 12.5141 | 192.3843 | 16.4633 | 194.2695 | 28.8217 | 20.0946 | 13.7395 | 197.3981 | 31.9758 | 11.9586 | 13.463 | 195.2366 | 18.2852 | 45.0188 | 13.8512 | 195.5067 | 18.7227 | 45.047 | 13.7651 | 196.953 | 194.1308 | 12.9628 | 45.1099 | 1.9145 | 9.9717 | 0 | 81.2157 | 21.6441 | 52.9644 | 13.1978 | 191.0645 | 193.9539 | 12.8508 | 3.3855 | 54.1556 | 108.7099 | 162.8654 | 12.4088 | 150.1123 | 103.0249 | 19.1148 | 8.886 | 85.0293 | 14.335 | 1.1016 | 0.20264 | 2.1187 | 96.2825 | 0.10578 | 0.19187 | 0.068008 | 0.08364 | 0.8527 | 0.39551
Total | MW: 828.0072; MVAR: 118.5699; kg/s: 3774793.4562; kg/s: 293720.8142; kg/s: 4297989.3454; kg/s: 8813875.7021; kg/s: 13111865.0475; kg/s: 12202479.1963
Average | 34.5003 | 4.9404 | 0.80052 | 0.81245 | 17.5525 | 4.3973 | 12.7736 | 193.2085 | 16.3595 | 193.9814 | 27.4956 | 21.3052 | 13.9712 | 197.8997 | 31.8886 | 10.9473 | 13.6914 | 195.7699 | 18.3952 | 45.0246 | 14.0384 | 196.0978 | 18.7926 | 45.6731 | 13.9799 | 197.4782 | 194.8081 | 13.1952 | 43.6897 | 2.978 | 9.9749 | 0 | 80.7615 | 21.858 | 50.7853 | 13.465 | 191.5209 | 194.6693 | 13.1026 | 3.3995 | 49.7452 | 102.0125 | 151.7577 | 12.1089 | 141.2324 | 96.3792 | 16.953 | 7.7377 | 86.9837 | 14.5879 | 0.92605 | 0.20269 | 1.7697 | 94.3282 | 0.11057 | 0.14092 | 2.7071 | 0.08799 | 0.79829 | 0.89892
Min | 33.8772 | 2.5448 | 0.74522 | 0.75268 | 15.4056 | 4.1224 | 12.5141 | 192.3843 | 15.8511 | 193.6366 | 25.2456 | 18.0315 | 13.7395 | 197.3981 | 31.6462 | 10.0577 | 13.463 | 195.2366 | 18.2852 | 45.0182 | 13.8512 | 195.5067 | 18.6924 | 45.047 | 13.7651 | 196.953 | 194.0947 | 12.9628 | 43.1425 | 1.9145 | 9.9676 | 0 | 79.1512 | 21.6441 | 49.3536 | 13.1978 | 191.0628 | 193.9331 | 12.8508 | 2.7142 | 46.4436 | 91.7273 | 140.8195 | 11.4976 | 133.1002 | 94.9595 | 14.6052 | 6.5054 | 85.0293 | 14.1826 | 0.74605 | 0.16448 | 1.4589 | 93.3134 | 0.10578 | 0.11198 | 0.068008 | 0.08364 | 0.49477 | 0.39512
Max | 35.0376 | 7.192 | 0.87721 | 0.89711 | 20.4579 | 4.7152 | 12.9662 | 193.8445 | 17.4487 | 194.6316 | 28.8217 | 29.6277 | 14.3685 | 198.9685 | 31.9779 | 12.0076 | 13.9545 | 196.4801 | 18.5389 | 45.0322 | 14.2633 | 196.8129 | 18.9361 | 46.1072 | 14.2067 | 198.1692 | 195.4312 | 13.3927 | 45.1099 | 3.5495 | 9.9911 | 0 | 81.8606 | 21.9935 | 53.0777 | 13.6805 | 192.1647 | 195.2758 | 13.2886 | 3.7143 | 54.1556 | 113.8111 | 165.21 | 13.4713 | 150.5078 | 103.0249 | 21.0836 | 8.886 | 87.6469 | 15.6949 | 1.1016 | 0.22882 | 2.1187 | 96.2825 | 0.11869 | 0.19187 | 18.6963 | 0.094154 | 1.5858 | 1.9402

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1
18 |  | Night | 22:15 | 5.55 | 22.2
19 | 2025-06-10 | Day | 8:55 | 5.69 | 31.6
20 |  | Night | 0:20 | 5.18 | 24.3
21 | 2025-06-11 | Day | 17:00 | 5.07 | 21.6
22 |  | Night | 22:30 | 5.62 | 28.8
23 | 2025-06-12 | Day | 10:10 | 5.08 | 27.3
24 |  | Night | 21:30 | 5.64 | 26.6
25 | 2025-06-13 | Day | 8:40 | 5.11 | 27.1
26 |  | Night | 22:00 | 5.77 | 25.5
27 | 2025-06-14 | Day | 10:00 | 5.55 | 32
28 |  | Night | 22:00 | 5.78 | 28.9
29 | 2025-06-15 | Day | 10:00 | 5.33 | 24.6
30 |  | Night | 23:45 | 5.82 | 30.3
31 | 2025-06-16 | Day | 9:40 | 5.44 | 27.9
32 |  | Night | 23:45 | 5.97 | 23.8
33 | 2025-06-17 | Day | 15:30 | 5.77 | 33
34 |  | Night | 22:45 | 5.86 | 27.7
35 | 2025-06-18 | Day | 10:35 | 5 | 21
36 |  | Night | 23:30 | 5.97 | 21.6
37 | 2025-06-19 | Day | 18:05 | 5.47 | 21.3
38 |  | Night | 23:45 | 5.41 | 31.3
39 | 2025-06-20 | Day
40 |  | Night
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-19
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0