## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-20
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 27.9735 | 197.6521 | 20.3759
|  | #6-2 | Production | 32.043 | 195.4866 | 10.2641
|  | #6-3 | Production | 18.3727 | 195.7737 | 45.0065
|  | #6-4 | Production | 18.7709 | 197.1001 | 45.6603
|  | #8-1 | Shut in | 0.7535 | 81.4807 | 9.9738
|  | #8-2 | Production | 21.4912 | 191.1774 | 53.4572
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 45.7936 | 3956568.048
|  | PAD #8 - STEAM |  |  |  |  | 3.4915 | 301666.3117 | Online
|  | BRINE HEADER |  |  |  |  | 89.1536 | 7702870.7229 | Offline
|  | TOTAL FLOW |  |  |  |  | 138.4387 | 11961105.0826
|  | PRESS SEPARATOR IJN 6 | Online | 13.1232 | 194.5706
|  | PRESS SEPARATOR IJN 8 | Online | 13.0087 | 194.3437
| INJECTION WELL | #5-1 | Injection | 6.5062 | 95.5817 | 15.1245 | 132.766 | 11470979.6224
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.9329 |  |  | 838.3885
|  | NET | 32.2622 |  |  | 774.2934
| PARASITIC LOAD |  | 2.6706 |  |  | 64.0951
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 3.963 |  |  | 14266.7813
|  | NET | 4.291 |  |  | 15447.7687
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 6. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
7. Brine Dump Control valve Ijen-6 PV-2227A indication passing
8. Compressor A have indication noise on bearing screw pump

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-20
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 774293.3848 |  | 0 |  | 774293.3848
|  |  |  | 774293.3848 |  | 0 |  | 774293.3848
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 777020 | [7 empty] | 777020
M-T-D GROSS GENERATION (kWHR) |  |  |  | 16527740 | [7 empty] | 16527740
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 18856.94 | 27687.25 | 3967.06 | 42.6 | 754 | 729 | 24349.6
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 367518.07 | 3160725.11 | 100907.85 | 869.7 | 22411 | 25396 | 149584.55
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.9329 |  |  | 5.7342 |  | 17.2628
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 480
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 93.52%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 3956.568 |  | 301.6663 |  |  | 4328.4098
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.045794 |  | 0.0034915 |  |  | 0.050097
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 7702.8707
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.089154
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 12031.2805
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.13925
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 192.8354 |  |  |  | 193.6209
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.6629 |  |  |  | 15.9407
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 15.1291 |  | 19.064 |  |  | 17.2628
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
6. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
7. Brine Dump Control valve Ijen-6 PV-2227A indication passing
8. Compressor A have indication noise on bearing screw pump
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
0:15 | Top up plan 53B barrel on BBP IJN 6 B
8:00 | Dispatch adviced load ROH 32.09 MW (Mr. M. Bahrul)
8:15 | Daily tool box meeting
9:52 | Running test jockey pump (Standart activities schedule)
10:05 | MOV IJN 5-1 (PV-2705A) Online Stroking Test (Standart activities schedule)
10:06 | Main Fire Pump and Diesel fire pump Testing (Standart activities schedule)
10:10 | Master valve IW IJN 5-1 exercise (Standart activities schedule)
10:15 | Turn off CB fire diesel fire pump due to repair leakage oil by MTC team
10:35 | Reinjection Pump B/P Control Valve (PV-2605) Offline Stroke Test (Standart activities schedule)
10:40 | Master valve PW IJN 9-1 exercise (Standart activities schedule)
13:45 | P8202 Fire Water Refilling pump run test (Standart activities schedule)
13:53 | Finishing troubleshoot streetlighting by MTC team
13:59 | Dispatch adviced load ROH 32.09 MW (Mr. M. Bahrul)
14:57 | Master valve IW IJN 2-1 exercise (Standart activities schedule)
15:15 | Install gasket seal plan 53B Brine Booster Pump B IJN 8 by MTC team
16:00 | Inspection of auxilliary trafo (Standart activities schedule)
19:45 | Handover day shift to night shift
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Hary |  |  |  | CCR Operator : Ois |  |  |  | Steamfield : Dadan
Night Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Fauzan |  |  |  | Steamfield : Vandy

## Meter
DATE: | 2025-06-20
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2255840 | 2259920 | 4080 | 132070
(BACKUP) |  | 2126290 | 2254120 | 2258200 | 4080 | 131910
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 107533030 | 108310050 | 777020 | 15208140
(BACKUP) |  | 93082960 | 107509990 | 108286780 | 776790 | 15203820
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4746040 | 4774940 | 28900 | 632710
(BACKUP) |  | 4144060 | 4748060 | 4776970 | 28910 | 632910
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 117008319 | 117850995 | 842676 | 16527740
TOTAL |  |  |  |  | 842676 | 16527740
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 19138991 | 19278783 | 139792 | 2748528
TOTAL |  |  |  |  | 139792 | 2748528
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3437979.47 | 3456836.41 | 18856.94 | 367518.07
U3B |  | 283254.3 | 3416292.16 | 3443979.41 | 27687.25 | 3160725.11
U3C |  | 989758.41 | 1086699.2 | 1090666.26 | 3967.06 | 100907.85
U Ijen 5 |  | 7258.6 | 8085.7 | 8128.3 | 42.6 | 869.7
U Ijen 6 |  | 247889 | 269546 | 270300 | 754 | 22411
U Ijen 8 |  | 299837 | 324504 | 325233 | 729 | 25396
TOTAL |  |  |  |  | 52036.85 | 517102.62
Note on E42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on G42: Operator MPGS: - Butuh konfirmasi setelah reading 1.000.000 kWh apakah reset value ?
Note on E43: Operator MPGS: - Power meter already reading on 17 June 2025 - Initial value following U3A on 3 Millions
Note on G43: Operator MPGS: - Power meter already reading on 17 June 2025 - Initial value following U3A on 3 Millions

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater |  | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Delta Pressure | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | oC | Bara | % | % | Barg | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | TT-2601 | PT-2603 | PV-2503A | PV-2503B | PV-2503 | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-20 01:00 | 35.2961 | 5.0997 | 0.76333 | 0.77123 | 15.4042 | 4.0469 | 12.769 | 193.2027 | 15.7899 | 193.832 | 29.6988 | 19.5906 | 13.9684 | 198.0867 | 31.9861 | 11.9584 | 13.6986 | 195.8013 | 18.3387 | 44.9729 | 14.0725 | 196.0242 | 18.8057 | 44.9907 | 13.992 | 197.559 | 194.9199 | 13.2242 | 45.6111 | 1.5729 | 9.974 | 0 | 81.1055 | 21.6591 | 52.3634 | 13.4414 | 191.3695 | 194.7042 | 13.1084 | 3.5536 | 51.0296 | 91.8107 | 142.8403 | 10.7879 | 134.7268 | 96.6365 | 17.9428 | 7.2927 | 86.032 | 14.0514 | 1.0434 | 0.20451 | 1.7431 | 93.6425 | 0.10598 | 0.18368 | 0.067758 | 0.083512 | 1.6819 | 0.39519
2025-06-20 02:00 | 35.294 | 3.4269 | 0.77014 | 0.77874 | 15.1291 | 3.8881 | 12.7836 | 193.2478 | 15.6644 | 193.7979 | 29.7281 | 19.51 | 13.9681 | 198.1311 | 31.9928 | 11.5698 | 13.7108 | 195.8518 | 18.3842 | 44.9843 | 14.0866 | 196.077 | 18.8484 | 44.9878 | 14.0063 | 197.5961 | 194.9906 | 13.2475 | 46.1933 | 1.3992 | 9.9731 | 0 | 81.0101 | 21.6661 | 52.2815 | 13.4588 | 191.3781 | 194.7482 | 13.1254 | 3.8304 | 50.341 | 86.8841 | 137.2252 | 11.1542 | 131.0085 | 95.2697 | 15.8463 | 6.698 | 84.8053 | 14.1111 | 0.96448 | 0.20538 | 1.5575 | 92.6773 | 0.10591 | 0.187 | 0.06785 | 0.083593 | 1.9357 | 0.39553
2025-06-20 03:00 | 35.2946 | 3.8039 | 0.76771 | 0.77828 | 15.1821 | 3.8685 | 12.7895 | 193.2685 | 15.6464 | 193.8627 | 29.3979 | 19.1289 | 13.9668 | 198.1251 | 32.0043 | 10.6654 | 13.716 | 195.8839 | 18.3692 | 45.0415 | 14.0887 | 196.0851 | 18.8952 | 45.0426 | 14.0113 | 197.5873 | 195.0136 | 13.2543 | 46.1696 | 1.3258 | 9.97 | 0 | 80.9322 | 21.6683 | 52.1686 | 13.4688 | 191.3978 | 194.7584 | 13.1311 | 3.6281 | 50.6367 | 85.8993 | 136.5361 | 11.4042 | 130.4244 | 94.6225 | 14.922 | 6.4928 | 84.1432 | 14.098 | 0.94382 | 0.20498 | 1.5468 | 92.5024 | 0.10601 | 0.18521 | 0.068048 | 0.08375 | 1.7161 | 0.39534
2025-06-20 04:00 | 35.2954 | 5.735 | 0.75801 | 0.76919 | 15.297 | 3.8406 | 12.787 | 193.2676 | 15.6428 | 193.8441 | 29.1526 | 19.0245 | 13.9587 | 198.0962 | 32.0133 | 10.149 | 13.7106 | 195.855 | 18.3442 | 45.0413 | 14.0819 | 196.0583 | 18.9138 | 45.0444 | 14.0047 | 197.5728 | 195.009 | 13.2506 | 46.023 | 1.2836 | 9.9697 | 0 | 80.8577 | 21.664 | 52.338 | 13.4656 | 191.3769 | 194.7489 | 13.128 | 3.3905 | 49.9972 | 85.5595 | 135.5567 | 11.2155 | 130.1562 | 94.5101 | 14.9221 | 6.3231 | 84.1274 | 14.0798 | 0.93956 | 0.20384 | 1.5616 | 92.4138 | 0.10617 | 0.18037 | 0.068024 | 0.083777 | 1.6638 | 0.39384
2025-06-20 05:00 | 35.2511 | 6.8174 | 0.75659 | 0.76631 | 15.2606 | 3.841 | 12.7834 | 193.2505 | 15.6613 | 193.8187 | 28.949 | 19.0185 | 13.9427 | 198.0585 | 32.0129 | 10.1483 | 13.7023 | 195.8319 | 18.3599 | 45.0399 | 14.0769 | 196.047 | 18.9039 | 45.0419 | 13.9964 | 197.5436 | 194.9866 | 13.2445 | 45.9749 | 1.2545 | 9.966 | 0 | 80.7673 | 21.657 | 52.2634 | 13.4579 | 191.3657 | 194.7333 | 13.124 | 3.4529 | 49.8713 | 85.5295 | 135.4008 | 11.1165 | 130.2199 | 94.5767 | 14.922 | 6.2093 | 84.0345 | 14.0829 | 0.94021 | 0.20285 | 1.5769 | 92.5334 | 0.10594 | 0.18561 | 0.067686 | 0.083511 | 1.6503 | 0.39322
2025-06-20 06:00 | 35.1758 | 6.7659 | 0.7559 | 0.76486 | 15.6164 | 3.8895 | 12.7589 | 193.1784 | 15.634 | 193.8247 | 28.7664 | 19.0166 | 13.9106 | 197.9717 | 32.0148 | 10.146 | 13.6742 | 195.779 | 18.3368 | 45.0403 | 14.0455 | 195.9789 | 18.8964 | 45.0441 | 13.9698 | 197.4632 | 194.9113 | 13.2182 | 45.9257 | 1.2249 | 9.9664 | 0 | 80.708 | 21.6553 | 52.1975 | 13.4357 | 191.3715 | 194.6651 | 13.0999 | 3.4016 | 51.5571 | 85.2584 | 136.8156 | 11.0275 | 130.089 | 94.7049 | 14.922 | 6.1288 | 83.8509 | 14.0483 | 0.93463 | 0.206 | 1.5838 | 92.641 | 0.1062 | 0.18124 | 0.06794 | 0.083716 | 1.4998 | 0.3965
2025-06-20 07:00 | 35.1297 | 6.6367 | 0.76959 | 0.77743 | 16.4063 | 3.9021 | 12.7307 | 193.0723 | 15.6283 | 193.7823 | 28.6211 | 19.0328 | 13.8918 | 197.8745 | 32.0267 | 10.1318 | 13.6503 | 195.6988 | 18.3428 | 45.0208 | 14.0056 | 195.9135 | 18.9088 | 45.0547 | 13.9491 | 197.3821 | 194.8156 | 13.1931 | 45.9261 | 1.2063 | 9.9716 | 0 | 80.7446 | 21.6681 | 52.6932 | 13.4214 | 191.3221 | 194.5719 | 13.0737 | 3.5788 | 51.1852 | 85.8949 | 137.0801 | 11.0642 | 130.4686 | 94.5696 | 14.9231 | 6.1296 | 83.9359 | 14.0591 | 0.91672 | 0.21295 | 1.5679 | 92.5636 | 0.10762 | 0.15514 | 0.069667 | 0.085472 | 1.4414 | 0.40249
2025-06-20 08:00 | 34.9351 | 6.4459 | 0.80723 | 0.80763 | 17.4322 | 3.8782 | 12.6792 | 192.8998 | 15.643 | 193.6599 | 28.5006 | 19.4956 | 13.867 | 197.7195 | 32.0475 | 10.1105 | 13.6126 | 195.5612 | 18.3658 | 45.0045 | 13.951 | 195.8188 | 18.9062 | 45.0745 | 13.9079 | 197.2666 | 194.6578 | 13.1471 | 46.0441 | 1.2339 | 9.9751 | 0 | 80.8899 | 21.6858 | 52.9583 | 13.3919 | 191.2373 | 194.4107 | 13.0238 | 3.7609 | 49.9633 | 85.5228 | 135.4861 | 11.031 | 130.57 | 94.7299 | 14.9253 | 6.086 | 84.1566 | 14.0844 | 0.89 | 0.21067 | 1.5574 | 92.6599 | 0.10985 | 0.12398 | 0.072417 | 0.088326 | 1.1261 | 0.4018
2025-06-20 09:00 | 34.9286 | 6.0518 | 0.82074 | 0.82109 | 18.0051 | 3.8405 | 12.671 | 192.8669 | 15.4875 | 193.6121 | 28.2794 | 20.7057 | 13.8852 | 197.7114 | 32.0663 | 10.0949 | 13.619 | 195.5294 | 18.3778 | 45.0079 | 13.9457 | 195.8276 | 18.8925 | 45.1511 | 13.9069 | 197.2663 | 194.6352 | 13.1441 | 46.2053 | 1.2947 | 9.9782 | 0 | 81.0708 | 21.6871 | 53.1074 | 13.3976 | 191.2389 | 194.3672 | 13.0162 | 3.6951 | 48.9479 | 85.1949 | 134.1428 | 10.4103 | 130.619 | 94.9055 | 13.1981 | 6.038 | 84.3593 | 13.8798 | 0.90314 | 0.20026 | 1.6087 | 93.0311 | 0.1114 | 0.11113 | 0.074086 | 0.089942 | 1.074 | 0.3938
2025-06-20 10:00 | 35.1782 | 6.0098 | 0.81698 | 0.82886 | 18.4328 | 3.9209 | 12.726 | 193.0302 | 15.7037 | 193.7623 | 27.9255 | 21.1 | 13.9709 | 197.9292 | 32.0793 | 10.0828 | 13.6929 | 195.7222 | 18.3823 | 45.0062 | 14.0074 | 196.0188 | 18.9013 | 45.6416 | 13.9799 | 197.4027 | 194.8167 | 13.2077 | 46.4202 | 1.2884 | 9.9796 | 0 | 81.2667 | 21.6818 | 54.0298 | 13.4706 | 191.4493 | 194.5464 | 13.0762 | 3.6665 | 50.9881 | 86.9421 | 137.9302 | 10.2198 | 132.1307 | 95.028 | 12.9433 | 6.1874 | 84.565 | 14.0454 | 0.84274 | 0.19324 | 1.6614 | 93.3885 | 0.11229 | 0.11037 | 0.074906 | 0.090575 | 1.3229 | 0.38922
2025-06-20 11:00 | 35.1127 | 5.3681 | 0.81916 | 0.83527 | 18.4912 | 4.0678 | 12.7195 | 193.0221 | 16.2967 | 193.7754 | 27.4257 | 20.3998 | 13.9758 | 197.8408 | 32.0936 | 10.0771 | 13.6883 | 195.7505 | 18.4326 | 45.0034 | 14.0085 | 196.0564 | 18.9191 | 46.068 | 13.9776 | 197.4047 | 194.7702 | 13.191 | 45.8327 | 1.2482 | 9.9827 | 0 | 81.4706 | 21.6076 | 54.7926 | 13.4739 | 191.5067 | 194.55 | 13.0699 | 3.6593 | 51.3889 | 91.4422 | 142.8311 | 11.1234 | 134.9574 | 95.6213 | 14.8477 | 6.634 | 84.93 | 14.59 | 0.75275 | 0.18118 | 1.707 | 93.6583 | 0.11283 | 0.11063 | 0.36894 | 0.090901 | 1.3552 | 0.38502
2025-06-20 12:00 | 35.0575 | 4.858 | 0.81473 | 0.82992 | 18.3422 | 4.0471 | 12.6772 | 192.8816 | 16.2763 | 193.7528 | 27.4902 | 20.0711 | 13.9337 | 197.6937 | 32.0964 | 10.0771 | 13.6443 | 195.6142 | 18.4449 | 45.0013 | 13.9706 | 195.9503 | 18.8018 | 46.0675 | 13.9294 | 197.3269 | 194.63 | 13.1469 | 45.7732 | 1.1661 | 9.9823 | 0 | 81.6374 | 21.4803 | 55.2259 | 13.4262 | 191.3883 | 194.4068 | 13.0254 | 3.6009 | 50.7515 | 91.131 | 141.8825 | 11.3072 | 134.5645 | 95.9136 | 15.2766 | 6.71 | 85.0412 | 14.5695 | 0.75296 | 0.17826 | 1.7051 | 93.6563 | 0.11268 | 0.11048 | 0.36885 | 0.090578 | 1.2844 | 0.38243
2025-06-20 13:00 | 35.0676 | 5.8295 | 0.82131 | 0.83809 | 18.8191 | 3.9966 | 12.6499 | 192.7836 | 15.9719 | 193.6669 | 27.7601 | 20.0727 | 13.9117 | 197.7016 | 32.0741 | 10.0784 | 13.6243 | 195.5086 | 18.3977 | 44.9995 | 13.9446 | 195.8769 | 18.6744 | 46.0677 | 13.9055 | 197.2175 | 194.5801 | 13.1322 | 46.4115 | 0.96168 | 9.9796 | 0 | 81.7782 | 21.4217 | 55.7726 | 13.3996 | 191.3227 | 194.3255 | 13.001 | 3.4969 | 52.8132 | 87.337 | 140.1502 | 10.8795 | 132.3517 | 95.6687 | 15.2766 | 6.4268 | 84.9728 | 14.3085 | 0.75628 | 0.1843 | 1.6619 | 93.5507 | 0.11249 | 0.11013 | 0.075059 | 0.090435 | 1.168 | 0.38287
2025-06-20 14:00 | 34.9649 | 6.4525 | 0.82715 | 0.84479 | 19.064 | 3.9484 | 12.6513 | 192.8053 | 15.8847 | 193.5814 | 27.5962 | 20.074 | 13.9045 | 197.6991 | 32.0722 | 10.08 | 13.6211 | 195.4926 | 18.4073 | 44.9984 | 13.9343 | 195.8688 | 18.6886 | 46.0683 | 13.8975 | 197.1129 | 194.5949 | 13.1313 | 46.4273 | 0.73752 | 9.98 | 0 | 81.9101 | 21.4036 | 55.698 | 13.3974 | 191.3217 | 194.3472 | 13.0018 | 3.5019 | 51.7116 | 86.3446 | 138.0562 | 10.6881 | 131.5991 | 95.5925 | 15.2769 | 6.2739 | 84.7755 | 14.2139 | 0.75972 | 0.18155 | 1.6692 | 93.5006 | 0.11232 | 0.10999 | 0.074961 | 0.090358 | 1.0721 | 0.38133
2025-06-20 15:00 | 34.7032 | 5.592 | 0.81539 | 0.83277 | 18.8214 | 4.0624 | 12.6582 | 192.8072 | 16.3027 | 193.5716 | 27.1054 | 20.0829 | 13.8777 | 197.5399 | 32.0503 | 10.0822 | 13.5986 | 195.4296 | 18.4224 | 45.0019 | 13.913 | 195.7936 | 18.7127 | 46.0703 | 13.874 | 196.9474 | 194.5155 | 13.1132 | 45.2615 | 0.48507 | 9.9793 | 0 | 82.0008 | 21.3818 | 55.1517 | 13.3921 | 191.2723 | 194.3209 | 13.0026 | 3.537 | 48.4567 | 92.5226 | 140.9793 | 11.3993 | 134.8197 | 95.6332 | 15.2281 | 6.6107 | 84.8893 | 14.5386 | 0.77289 | 0.17985 | 1.7622 | 93.9195 | 0.11137 | 0.10978 | 0.16049 | 0.08958 | 0.90627 | 0.38116
2025-06-20 16:00 | 34.7024 | 4.9318 | 0.80587 | 0.82252 | 18.5683 | 4.0747 | 12.6454 | 192.7589 | 16.3104 | 193.5991 | 27.2321 | 20.0972 | 13.8513 | 197.4745 | 32.0142 | 10.0879 | 13.5748 | 195.3854 | 18.4047 | 45.0061 | 13.8961 | 195.7446 | 18.6924 | 46.0619 | 13.8541 | 196.8853 | 194.4526 | 13.0941 | 45.0009 | 0.17619 | 9.9738 | 0 | 82.0464 | 21.3564 | 53.9894 | 13.3697 | 191.2238 | 194.2653 | 12.9888 | 3.4223 | 47.9417 | 93.4592 | 141.4009 | 12.0282 | 135.3412 | 95.9844 | 14.9749 | 6.7592 | 84.7521 | 14.5426 | 0.79073 | 0.1826 | 1.766 | 94.0048 | 0.10991 | 0.11191 | 0.15909 | 0.088341 | 0.80584 | 0.38206
2025-06-20 17:00 | 34.6936 | 6.3479 | 0.80373 | 0.81786 | 18.4751 | 3.9914 | 12.6134 | 192.6613 | 15.9677 | 193.6039 | 27.1882 | 20.107 | 13.8068 | 197.4284 | 32.0227 | 10.0922 | 13.5409 | 195.3166 | 18.3711 | 45.0062 | 13.8666 | 195.6665 | 18.6639 | 46.0471 | 13.825 | 196.7999 | 194.3798 | 13.0667 | 45.3917 | 0.023626 | 9.9716 | 0 | 82.0616 | 21.3357 | 53.2467 | 13.3334 | 191.1484 | 194.1785 | 12.9591 | 3.3041 | 48.7522 | 89.7248 | 138.477 | 11.915 | 132.9382 | 95.9978 | 14.7699 | 6.4879 | 84.5169 | 14.2582 | 0.80139 | 0.18544 | 1.708 | 93.7118 | 0.10891 | 0.11774 | 0.071323 | 0.087299 | 0.86947 | 0.38221
2025-06-20 18:00 | 34.6902 | 7.0765 | 0.80249 | 0.81305 | 18.3895 | 4.0673 | 12.6204 | 192.6909 | 16.2309 | 193.4785 | 27.1883 | 20.6617 | 13.8062 | 197.428 | 32.0297 | 10.0925 | 13.5413 | 195.3478 | 18.3982 | 45.0049 | 13.8711 | 195.6699 | 18.6819 | 46.0427 | 13.8296 | 196.8147 | 194.391 | 13.0683 | 45.1644 | 0.022078 | 9.9742 | 0 | 82.0598 | 21.3303 | 53.2693 | 13.3355 | 191.1284 | 194.198 | 12.9655 | 3.2875 | 48.872 | 92.2227 | 141.0947 | 12.2214 | 134.4423 | 95.9547 | 14.7688 | 6.6605 | 84.7256 | 14.4702 | 0.80515 | 0.18752 | 1.7591 | 93.8773 | 0.10846 | 0.12232 | 0.72963 | 0.086742 | 0.96027 | 0.38096
2025-06-20 19:00 | 34.9541 | 6.6356 | 0.80043 | 0.81103 | 17.8212 | 3.9801 | 12.6519 | 192.7969 | 16.1729 | 193.5237 | 27.6825 | 21.626 | 13.8509 | 197.6054 | 32.0311 | 10.0941 | 13.5805 | 195.4571 | 18.3772 | 45.0025 | 13.9093 | 195.7489 | 18.6715 | 46.0431 | 13.8674 | 196.9425 | 194.5317 | 13.111 | 45.7245 | 0.02537 | 9.9701 | 0 | 82.055 | 21.3213 | 53.1792 | 13.3636 | 191.1842 | 194.3046 | 12.9984 | 3.5095 | 49.271 | 89.8491 | 139.1201 | 12.0555 | 133.204 | 96.3984 | 14.7678 | 6.5736 | 84.2095 | 14.4204 | 0.8027 | 0.18928 | 1.7509 | 93.6217 | 0.10816 | 0.12624 | 0.72956 | 0.086409 | 0.96601 | 0.37937
2025-06-20 20:00 | 34.5344 | 5.9316 | 0.80796 | 0.82211 | 16.9193 | 4.0213 | 12.5724 | 192.5301 | 16.0891 | 193.5169 | 27.0087 | 22.0413 | 13.7456 | 197.2823 | 32.0403 | 10.0982 | 13.4868 | 195.1695 | 18.3536 | 44.9977 | 13.8236 | 195.4885 | 18.6421 | 46.046 | 13.7794 | 196.6333 | 194.2316 | 13.0186 | 45.3514 | 0.026687 | 9.9681 | 0 | 82.0161 | 21.3121 | 53.1808 | 13.286 | 190.9273 | 194.0368 | 12.9189 | 3.5452 | 48.4762 | 90.3957 | 138.8719 | 11.9691 | 133.0374 | 95.8272 | 14.767 | 6.4489 | 83.9318 | 14.3247 | 0.80512 | 0.18925 | 1.763 | 93.7275 | 0.10765 | 0.13404 | 1.0551 | 0.085683 | 0.86241 | 0.37782
2025-06-20 21:00 | 34.3433 | 4.7531 | 0.85504 | 0.8671 | 16.9945 | 4.1497 | 12.4904 | 192.2472 | 16.2845 | 193.3246 | 27.012 | 22.0448 | 13.6687 | 197.0194 | 32.0509 | 10.1027 | 13.4079 | 194.9243 | 18.3799 | 44.9944 | 13.7527 | 195.2482 | 18.6607 | 46.0468 | 13.7065 | 196.3904 | 193.9393 | 12.932 | 45.3897 | 0.027812 | 9.9729 | 0 | 81.9288 | 21.3019 | 53.2574 | 13.2082 | 190.6217 | 193.7527 | 12.8396 | 3.2999 | 49.5228 | 92.9925 | 142.5153 | 12.3654 | 134.7234 | 96.1116 | 14.7662 | 6.7088 | 84.0348 | 14.4676 | 0.81167 | 0.18842 | 1.8155 | 94.3126 | 0.1072 | 0.1413 | 1.0553 | 0.084933 | 0.82483 | 0.37591
2025-06-20 22:00 | 34.3929 | 5.3973 | 0.88081 | 0.88977 | 17.3484 | 4.1177 | 12.4896 | 192.2471 | 16.1143 | 193.1745 | 27.1581 | 22.0434 | 13.6707 | 197.065 | 32.0586 | 10.1055 | 13.4102 | 194.9181 | 18.3091 | 44.9939 | 13.7488 | 195.196 | 18.6395 | 46.0464 | 13.7069 | 196.4307 | 193.9646 | 12.9383 | 45.7395 | 0.029705 | 9.9734 | 0 | 81.8278 | 21.2876 | 53.2644 | 13.2078 | 190.5828 | 193.7582 | 12.8408 | 3.2396 | 50.7695 | 90.8508 | 141.6203 | 11.5236 | 133.3986 | 96.4805 | 15.549 | 6.627 | 83.9865 | 14.3161 | 0.81376 | 0.18768 | 1.7966 | 94.3319 | 0.10709 | 0.14366 | 0.069273 | 0.084832 | 0.82493 | 0.37474
2025-06-20 23:00 | 34.4204 | 6.2126 | 0.85025 | 0.85702 | 17.3295 | 4.15 | 12.4964 | 192.2696 | 16.0283 | 193.2213 | 27.0877 | 22.0405 | 13.6722 | 197.0289 | 32.0673 | 10.1067 | 13.4075 | 194.9019 | 18.2984 | 44.9939 | 13.7423 | 195.1747 | 18.5931 | 46.0489 | 13.7029 | 196.4115 | 193.9502 | 12.9357 | 45.1814 | 0.033257 | 9.9704 | 0 | 81.7387 | 21.2795 | 53.271 | 13.2131 | 190.5737 | 193.7722 | 12.8449 | 3.2326 | 49.3762 | 93.4691 | 142.8453 | 10.9278 | 134.8202 | 96.7364 | 16.5283 | 6.7797 | 83.5942 | 14.1748 | 0.81287 | 0.18951 | 1.852 | 94.1644 | 0.10721 | 0.14087 | 0.06953 | 0.085098 | 0.81656 | 0.37664
2025-06-21 | 34.973 | 5.4417 | 0.77958 | 0.79522 | 16.7578 | 4.0935 | 12.4949 | 192.2643 | 16.1455 | 193.3148 | 27.4085 | 22.0365 | 13.6771 | 197.1394 | 32.0876 | 10.1066 | 13.4138 | 194.9479 | 18.3461 | 44.9922 | 13.7517 | 195.2371 | 18.5873 | 46.0493 | 13.7085 | 196.4459 | 194.0057 | 12.9472 | 45.9036 | 0.036598 | 9.9685 | 0 | 81.654 | 21.2758 | 53.2715 | 13.2146 | 190.548 | 193.7777 | 12.8459 | 3.2011 | 49.7147 | 93.4489 | 143.1636 | 10.9087 | 135.7726 | 96.4865 | 16.7234 | 6.8619 | 84.0976 | 14.2286 | 0.8071 | 0.19346 | 1.9143 | 97.1222 | 0.10755 | 0.14041 | 0.069897 | 0.085255 | 0.80592 | 0.37949
Total | MW: 838.3885; MVAR: 137.6214; kg/s: 3956568.048; kg/s: 301666.3117; kg/s: 4328409.7502; kg/s: 7702870.7229; kg/s: 12031280.4731; kg/s: 11470979.6224
Average | 34.9329 | 5.7342 | 0.80292 | 0.81417 | 17.2628 | 3.9869 | 12.6629 | 192.8354 | 15.9407 | 193.6209 | 27.9735 | 20.3759 | 13.8618 | 197.6521 | 32.043 | 10.2641 | 13.597 | 195.4866 | 18.3727 | 45.0065 | 13.9373 | 195.7737 | 18.7709 | 45.6603 | 13.887 | 197.1001 | 194.5706 | 13.1232 | 45.7936 | 0.7535 | 9.9738 | 0 | 81.4807 | 21.4912 | 53.4572 | 13.3763 | 191.1774 | 194.3437 | 13.0087 | 3.4915 | 50.0973 | 89.1536 | 139.2509 | 11.281 | 132.766 | 95.5817 | 15.1245 | 6.5062 | 84.4362 | 14.2485 | 0.84849 | 0.19346 | 1.6915 | 93.5505 | 0.1088 | 0.13889 | 0.23981 | 0.086776 | 1.1931 | 0.38662
Min | 34.3433 | 3.4269 | 0.7559 | 0.76486 | 15.1291 | 3.8405 | 12.4896 | 192.2471 | 15.4875 | 193.1745 | 27.0087 | 19.0166 | 13.6687 | 197.0194 | 31.9861 | 10.0771 | 13.4075 | 194.9019 | 18.2984 | 44.9729 | 13.7423 | 195.1747 | 18.5873 | 44.9878 | 13.7029 | 196.3904 | 193.9393 | 12.932 | 45.0009 | 0.022078 | 9.966 | 0 | 80.708 | 21.2758 | 52.1686 | 13.2078 | 190.548 | 193.7527 | 12.8396 | 3.2011 | 47.9417 | 85.1949 | 134.1428 | 10.2198 | 130.089 | 94.5101 | 12.9433 | 6.038 | 83.5942 | 13.8798 | 0.75275 | 0.17826 | 1.5468 | 92.4138 | 0.10591 | 0.10978 | 0.067686 | 0.083511 | 0.80584 | 0.37474
Max | 35.2961 | 7.0765 | 0.88081 | 0.88977 | 19.064 | 4.15 | 12.7895 | 193.2685 | 16.3104 | 193.8627 | 29.7281 | 22.0448 | 13.9758 | 198.1311 | 32.0964 | 11.9584 | 13.716 | 195.8839 | 18.4449 | 45.0415 | 14.0887 | 196.0851 | 18.9191 | 46.0703 | 14.0113 | 197.5961 | 195.0136 | 13.2543 | 46.4273 | 1.5729 | 9.9827 | 0 | 82.0616 | 21.6871 | 55.7726 | 13.4739 | 191.5067 | 194.7584 | 13.1311 | 3.8304 | 52.8132 | 93.4691 | 143.1636 | 12.3654 | 135.7726 | 96.7364 | 17.9428 | 7.2927 | 86.032 | 14.59 | 1.0434 | 0.21295 | 1.9143 | 97.1222 | 0.11283 | 0.187 | 1.0553 | 0.090901 | 1.9357 | 0.40249

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1
18 |  | Night | 22:15 | 5.55 | 22.2
19 | 2025-06-10 | Day | 8:55 | 5.69 | 31.6
20 |  | Night | 0:20 | 5.18 | 24.3
21 | 2025-06-11 | Day | 17:00 | 5.07 | 21.6
22 |  | Night | 22:30 | 5.62 | 28.8
23 | 2025-06-12 | Day | 10:10 | 5.08 | 27.3
24 |  | Night | 21:30 | 5.64 | 26.6
25 | 2025-06-13 | Day | 8:40 | 5.11 | 27.1
26 |  | Night | 22:00 | 5.77 | 25.5
27 | 2025-06-14 | Day | 10:00 | 5.55 | 32
28 |  | Night | 22:00 | 5.78 | 28.9
29 | 2025-06-15 | Day | 10:00 | 5.33 | 24.6
30 |  | Night | 23:45 | 5.82 | 30.3
31 | 2025-06-16 | Day | 9:40 | 5.44 | 27.9
32 |  | Night | 23:45 | 5.97 | 23.8
33 | 2025-06-17 | Day | 15:30 | 5.77 | 33
34 |  | Night | 22:45 | 5.86 | 27.7
35 | 2025-06-18 | Day | 10:35 | 5 | 21
36 |  | Night | 23:30 | 5.97 | 21.6
37 | 2025-06-19 | Day | 18:05 | 5.47 | 21.3
38 |  | Night | 23:45 | 5.41 | 31.3
39 | 2025-06-20 | Day | 17:56 | 5.5 | 26.5
40 |  | Night | 0:00 | 5.34 | 27.9
41 | 2025-06-21 | Day
42 |  | Night
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-20
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0