## Summary
DAILY REPORT PLTP IJEN UNIT-1 | [5 empty] | 2025-06-21
|  |  | WELL STATUS | WHP AVERAGE (barg) | TEMP AVERAGE (oC) | VALVE OPENING (%) | FLOW AVERAGE (kg/s) | TOTAL FLOW (kg)
| PRODUCTION WELL | #6-1 | Production | 26.579 | 198.1488 | 26.7962
|  | #6-2 | Production | 31.7467 | 195.6869 | 14.534
|  | #6-3 | Production | 18.6581 | 195.8781 | 43.6331
|  | #6-4 | Production | 18.8999 | 197.1732 | 44.4292
|  | #8-1 | Shut in | 0.0445 | 81.2592 | 9.9725
|  | #8-2 | Production | 21.3065 | 191.129 | 52.7933
|  | #9-1 | Shut in
| SAGS | PAD #6 - STEAM |  |  |  |  | 45.408 | 3923250.282
|  | PAD #8 - STEAM |  |  |  |  | 3.5267 | 304709.2919 | Online
|  | BRINE HEADER |  |  |  |  | 102.9535 | 8895178.2147 | Offline
|  | TOTAL FLOW |  |  |  |  | 151.8882 | 13123137.7886
|  | PRESS SEPARATOR IJN 6 | Online | 13.1369 | 194.6137
|  | PRESS SEPARATOR IJN 8 | Online | 13.0268 | 194.4138
| INJECTION WELL | #5-1 | Injection | 7.8683 | 96.6288 | 19.5283 | 141.4313 | 12219667.5845
|  | #2-1 | Shut in
| PARTICULAR |  | AVERAGE (MW/h) |  |  | TOTAL (MWh)
| GENERATION | GROSS | 34.8787 |  |  | 837.0881
|  | NET | 32.1683 |  |  | 772.0397
| PARASITIC LOAD |  | 2.7104 |  |  | 65.0485
| POWER PLANT EFFICIENCY (kg/Mwe) |  | (kg/MWs) |  |  | (kg/MW)
|  | GROSS | 4.3548 |  |  | 15677.1285
|  | NET | 4.7217 |  |  | 16998.0101
Notes:
1. Steam Dump Control Valve PV-2430B indication PV has passing problem
| 2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [7 empty] | Production
3 EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking. Status: CB open and manual valve suction & discharge close.
| 6. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking | [7 empty] | Injection
7. Brine Dump Control valve Ijen-6 PV-2227A indication passing
8. Compressor A have indication noise on bearing screw pump

## Report
DAILY GENERATION REPORT : PLTP IJEN UNIT-1 | [11 empty] | 2025-06-21
I.) DAILY NET GENERATION:
REVENUE METER |  |  |  | DAILY 2400 HOURS KWH METER READING
|  |  |  | Exported Power (kWH) |  | Imported Power ( kWH ) |  | Net Generation (kWH)
kWh Meter Utama |  |  |  | 772039.6523 |  | 0 |  | 772039.6523
|  |  |  | 772039.6523 |  | 0 |  | 772039.6523
II.) PLANT GROSS GENERATION/PARASITIC LOAD:
PARTICULAR |  |  |  | OEC |  | U3A | U3B | U3C | U ijen 5 | U Ijen 6 | Uijen 8 | TOTAL
DAILY GROSS GENERATION (kWHR) |  |  |  | 770680 | [7 empty] | 770680
M-T-D GROSS GENERATION (kWHR) |  |  |  | 17365765 | [7 empty] | 17365765
DAILY PARASITIC LOAD (kWHR) | [5 empty] | 29135.669 | 28068.06 | 4167.72 | 42.9 | 951 | 786 | 35083.289
M-T-D PARASITIC LOAD (kWHR) | [5 empty] | 396653.739 | 3188793.17 | 105075.57 | 912.6 | 23362 | 26182 | 155532.17
III.) PLANT PERFORMANCE / STEAM CONDITION
PARTICULAR | [5 empty] | PARAMETER
Active Gross Power Average / Reactive Gross Power Average/Ambient Temp | [5 empty] | 34.8787 |  |  | 5.2697 |  | 18.3913
Rated Unit Capacity | [5 empty] | 34.496
Service Hours | [5 empty] | 24
Month-to-Date Service Hours | [5 empty] | 504
Percent Availability Factor | [5 empty] | 100%
Percent Capacity Factor (Based on URC=XX MW) | [5 empty] | 93.25%
Valve Stem-Free Test (Pass/Fail/Not-on-scheduled) | [5 empty] | Not-on-scheduled
Steam Consumption, in kg (Sep A/SepB/Total) | [5 empty] | 3923.2503 |  | 304.7093 |  |  | 4440.1525
Daily Average Steam Flow, in kg/s (Sep A/Sep B/Total) | [5 empty] | 0.045408 |  | 0.0035267 |  |  | 0.051391
Brine Consumption, in kg/s (Sep A/SepB/Total) | [10 empty] | 8895.1782
Daily Average Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.10295
Steam - Brine consumption, in kg (Sep A/Sep B/Total) | [10 empty] | 13335.3307
Daily Average Steam - Brine Flow, in kg/s (Sep A/Sep B/Total) | [10 empty] | 0.15434
Daily Average Inlet Steam/Brine Temperature (°C) | [5 empty] | 192.9024 |  |  |  | 193.9696
Daily Average Inlet Steam /Brine Pressure (barg) | [5 empty] | 12.6829 |  |  |  | 16.5238
Ambient Temperature (°C)(Min/Max/Ave) | [5 empty] | 15.947 |  | 20.6612 |  |  | 18.3913
IV.) OUTAGE SUMMARY:
A.) PLANT FORCED OUTAGES:
Date |  | Outage Period |  | Unit # | ACTUAL FOH | ToP |  | Estimated MWH Lost | Cause | REMARKS
|  | From | To |  |  | MW
CAUSE: OF = OPERATION FAILURE MF = MECHANICAL FAILURE EF = ELECTRICAL FAILURE ID = INSTR'N/DCS FAILURE
B.) NO-FAULT OUTAGE: | [13 empty] | URC:
Unit |  | Curtailment Time |  |  |  | Curtailment load |  | Estimated Deemed Delivered Energy (MWh) |  | Cause | REMARKS
|  | DATE | Start | End | Duration hrs | Before (MW) | After (MW)
CAUSE: IF = INTERCONNECTION FAILURE MS = MATERIAL SHORTFALL SM = SCHEDULED MAINTENANCE FM = FORCE MAJEURE
V.) UNIT STATE
UNIT # |  | UNIT STATUS |  |  |  |  | FROM |  | TO |  | REMARKS
OEC |  | IN-SERVICE |  |  |  |  | 00:00 |  | 24:00
UNIT STATE: IN-SERVICE, UNDER MAINTENANCE, RESERVE SHUTDOWN, OTHERS
VI.) EQUIPMENT PROBLEMS, DOWNTIME, LONG TERM OPERATION IMPACT
1. Steam Dump Control Valve PV-2430B indication PV has passing problem (inprogress rectification)
2. Indication passing on manual valve to service line IJN 6-3 (HV-2008C) | [12 empty] | Production
3. EDG On load test need to set and rectified so not affect unit outages as per insurance compliance based on NFPA regulation No.110 section 8.4.2
4. LV-2227B set to manual mode because under maintenance, manual valve before LV close and LOTO.
5. Brine Booster Pump IJN-8B (P-2301B) have indication mechseal leaking
6. Brine Booster Pump IJN-6A (P-2201A) have indication mechseal leaking
7. Brine Dump Control valve Ijen-6 PV-2227A indication passing
8. Compressor A have indication noise on bearing screw pump
VII.) PLN GRID CONDITION, STEAM FIELD CONDITION, ADDITIONAL COMMENTS
VIII.) EVENT LOG
Time | Activities
8:05 | Dispatch adviced load ROH (Mr. Inggih)
8:15 | Daily tool box meeting
10:10 | Prepare taking sample of air in outlet NCG CW Side by AAS team
11:05 | Change over re-injection pump A to pump B due to high DP (0.62 barg)
11:20 | LOTO CB Re-injection pump A & Motor cooling sytem due to prepare cleaning strainer
13:10 | Take out strainer re-injection pump A from the bucket
13:30 | Change over GCW pump A to pump B
13:45 | Cleaning strainer Re-Injection pump A
14:50 | Inspection & validation Temperature transmitter OEC area by MTC team
14:52 | Install strainer re-injection pump A (After cleaning)
15:00 | Dispatch adviced load ROH (Mr. Ragil)
15:02 | Take out LOTO CB Re-injection pump A & Motor cooling system
17:02 | Manual rotate shaft Brine booster pump B IJN-8 (Pump Standby) due to ensure the shaft is not stuck
17:05 | Dump valve B IJN 8 (LV2327B) offline exercise and switch priority (Standart activities schedule)
17:18 | Manual rotate shaft Brine booster pump A IJN-6 (Pump Standby) due to ensure the shaft is not stuck
17:57 | pH Check and Release Dispossal Pond (Standart activities schedule)
19:45 | Handover day shift to night shift
20:20 | Change strainer brine inlet preheater SP2501B to SP2501A to check PDT on strainer A
20:45 | The PDT on SP2501A is higher than SP2501B (Indicated from brine inlet flow). Change strainer from SP2501A to SP2501B
21:00 | Depressurize and drain SP2501A due to preparation for cleaning
21:45 | Open strainer SP2501A and soaking the mesh for cleaning
IX.) SERVICE REQUEST
X.) SHIFT CREW
Day Shift | Shift Leader : Hary |  |  |  | CCR Operator : Ois |  |  |  | Steamfield : Dadan
Night Shift | Shift Leader : Mahatir |  |  |  | CCR Operator : Fauzan |  |  |  | Steamfield : Vandy

## Meter
DATE: | 2025-06-21
I.) IMPORTED POWER (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 294900 | 294900 | 294900 | 0 | 0
(BACKUP) |  | 301360 | 301360 | 301360 | 0 | 0
II.) IMPORTED POWER (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 2127850 | 2259920 | 2269050 | 9130 | 141200
(BACKUP) |  | 2126290 | 2258200 | 2267320 | 9120 | 141030
III.) EXPORTED ENERGY (KWH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 93101910 | 108310050 | 109080730 | 770680 | 15978820
(BACKUP) |  | 93082960 | 108286780 | 109057260 | 770480 | 15974300
IV.) EXPORTED ENERGY (KVARH)
REVENUE METER |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
(MAIN) |  | 4142230 | 4774940 | 4797940 | 23000 | 655710
(BACKUP) |  | 4144060 | 4776970 | 4799990 | 23020 | 655930
V.) GROSS ENERGY OUTPUT (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 101323255 | 117850995 | 118689020 | 838025 | 17365765
TOTAL |  |  |  |  | 838025 | 17365765
VI.) GROSS ENERGY OUTPUT (KVARH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
OEC |  | 16530255 | 19278783 | 19406414 | 127631 | 2876159
TOTAL |  |  |  |  | 127631 | 2876159
VII.) Houseload Consumption (KWH)
UNIT No. |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
U3A |  | 3089318.34 | 3456836.41 | 3485972.079 | 29135.669 | 396653.739
U3B |  | 283254.3 | 3443979.41 | 3472047.47 | 28068.06 | 3188793.17
U3C |  | 989758.41 | 1090666.26 | 1094833.98 | 4167.72 | 105075.57
U Ijen 5 |  | 7258.6 | 8128.3 | 8171.2 | 42.9 | 912.6
U Ijen 6 |  | 247889 | 270300 | 271251 | 951 | 23362
U Ijen 8 |  | 299837 | 325233 | 326019 | 786 | 26182
TOTAL |  |  |  |  | 63151.349 | 552185.909
Note on E42: Operator MPGS: - 21/06/2025, Karena kerusakan kabel current L2, maka pembacaan power tidak akurat. Tambahkan 9697.769
Note on G42: Operator MPGS: - 21/06/2025, Karena kerusakan kabel current L2, maka pembacaan power tidak akurat. Tambahkan 9697.769
Note on E43: Operator MPGS: - Power meter already reading on 17 June 2025 - Initial value following U3A on 3 Millions
Note on G43: Operator MPGS: - Power meter already reading on 17 June 2025 - Initial value following U3A on 3 Millions

## Steamfield
Hour of Day | Generation |  | OEC |  | Ambient Temp | Spesific Steam - Brine Consumption | Steam |  | Brine |  | IJN-6-1 |  |  |  | IJN-6-2 |  |  |  | IJN-6-3 |  |  |  | IJN-6-4 |  |  |  | PAD 6 |  |  | IJN-8-1 |  |  |  | IJN-8-2 |  |  |  | PAD 8 |  |  | Pad 6 & Pad 8 |  |  | IJN-5-1 |  |  |  |  | Header Reinjection Pump |  | Brine Bypass Pre-heater |  | Preheater |  | Separator IJN-6 |  | Separator IJN-8 |  | Rock Muffler
| Active Gross Power | Reactive Gross Power | Exhaust Pressure Turbine CW | Exhaust Pressure Turbine CCW |  |  | Main Steam Press | Main Steam Temp | Brine Header Press | Brine Header Temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | WHP | Valve Open | 2 Phase line press | 2 Phase line temp | Separator Temp | Separator Pressure | Steam Flow | Main Steam Flowrate | Brine Flowrate | Total Flowrate | Injection Press | Injection Flow | Injection Temp | Valve open | WHP | Header Reinjection Pump Temperature | Header Reinjection Pump Pressure | Opening CV-A | Opening CV-B | Delta Pressure | Outlet Temp | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Brine Dump Valve A | Opening Brine Dump Valve B | Opening Steam Dump Valve A | Opening Steam Dump Valve B
| MW | MVAR | Bara | Bara | oC | kg/MW | barg | oC | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | barg | % | barg | oC | barg | % | barg | oC | oC | barg | kg/s | kg/s | kg/s | kg/s | bara | kg/s | oC | % | barg | oC | Bara | % | % | Barg | oC | % | % | % | % | % | %
| WT | VART | PT9206 | PT9256 | TE93X0 |  | PT2504x | TT2501 | PT2503 | TT2502 | PT2006A | PV2005A | PT2008A | TT2007A | PT2006B | PV2005B | PT2008B | TT2007B | PT2006C | PV2005C | PT2008C | TT2007C | PT2006D | PV2005D | PT2008D | TT2007D | TT2207 | PT2208 | FT2220 | PT2106A | PV2105A | PT2108A | TT2107A | PT2106B | PV2105B | PT2108B | TT2107B | TT2307 | PT2308 | FT2320 | FT2527 | FT2505 |  | PT2702A | FT2703A | TT2704A | PV2705A | PT2703A | TT-2601 | PT-2603 | PV-2503A | PV-2503B | PV-2503 | TE-9124 | LV-2227A | LV-2227B | LV-2327A | LV-2327A | PV-2430A | PV-2430A
2025-06-21 01:00 | 34.4096 | 5.4515 | 0.84274 | 0.84661 | 16.8371 | 4.1678 | 12.5848 | 192.5692 | 16.0233 | 193.3264 | 27.0544 | 22.0404 | 13.7495 | 197.2761 | 32.0998 | 10.1071 | 13.4889 | 195.1377 | 18.3357 | 44.993 | 13.8258 | 195.3866 | 18.6148 | 46.0008 | 13.7805 | 196.6386 | 194.2448 | 13.024 | 44.9262 | 0.048433 | 9.9701 | 0 | 81.5398 | 21.2816 | 53.1677 | 13.2931 | 190.7709 | 194.076 | 12.93 | 3.5085 | 49.9031 | 93.5082 | 143.4113 | 10.5634 | 134.5009 | 95.6841 | 16.7229 | 6.5731 | 83.1295 | 14.1342 | 0.81556 | 0.18933 | 1.8878 | 93.4164 | 0.1069 | 0.14755 | 0.069149 | 0.084774 | 0.96588 | 0.37347
2025-06-21 02:00 | 34.4294 | 5.5544 | 0.80737 | 0.81347 | 16.2651 | 4.1544 | 12.6258 | 192.7157 | 16.0097 | 193.4565 | 27.0892 | 22.0425 | 13.7785 | 197.3795 | 32.1051 | 10.1102 | 13.5201 | 195.2249 | 18.3296 | 44.9927 | 13.8538 | 195.4647 | 18.6101 | 45.5034 | 13.8064 | 196.7803 | 194.3745 | 13.0607 | 44.6827 | 0.04772 | 9.9671 | 0 | 81.416 | 21.2786 | 53.0248 | 13.3283 | 190.8912 | 194.2132 | 12.9686 | 3.6214 | 49.3669 | 93.6647 | 143.0316 | 10.5375 | 134.3345 | 96.2754 | 16.723 | 6.5508 | 82.8763 | 14.0986 | 0.82173 | 0.19122 | 1.9098 | 93.5697 | 0.10657 | 0.15581 | 0.068706 | 0.084329 | 0.93031 | 0.37175
2025-06-21 03:00 | 34.5074 | 5.4518 | 0.77483 | 0.78996 | 16.0278 | 4.1311 | 12.6011 | 192.6217 | 15.9753 | 193.4814 | 27.0929 | 22.041 | 13.7529 | 197.2962 | 32.1151 | 10.1099 | 13.4938 | 195.1109 | 18.3353 | 44.9924 | 13.8251 | 195.3749 | 18.624 | 45.0542 | 13.7778 | 196.6719 | 194.2769 | 13.0341 | 44.592 | 0.045468 | 9.9688 | 0 | 81.3181 | 21.2831 | 53.0928 | 13.3058 | 190.8284 | 194.113 | 12.9437 | 3.6064 | 49.2598 | 93.2933 | 142.5531 | 10.4399 | 133.7973 | 95.5414 | 16.7234 | 6.4767 | 83.1335 | 14.0735 | 0.81753 | 0.19379 | 1.9004 | 93.7525 | 0.10667 | 0.15378 | 0.50151 | 0.084293 | 0.88321 | 0.37242
2025-06-21 04:00 | 34.4811 | 6.324 | 0.82283 | 0.82856 | 16.3094 | 4.2006 | 12.5384 | 192.4098 | 16.104 | 193.3291 | 27.0619 | 22.3824 | 13.7187 | 197.1764 | 32.1078 | 10.6097 | 13.4532 | 194.9754 | 18.3543 | 45.3382 | 13.7937 | 195.2962 | 18.7047 | 45.3828 | 13.7459 | 196.5318 | 194.0927 | 12.9788 | 45.0381 | 0.045004 | 9.9706 | 0 | 81.2342 | 21.2856 | 53.9429 | 13.2497 | 190.6449 | 193.911 | 12.8854 | 3.4457 | 50.0645 | 94.7771 | 144.8416 | 10.7476 | 135.5352 | 96.0614 | 16.7235 | 6.6908 | 83.3209 | 14.1544 | 0.81584 | 0.19223 | 1.948 | 94.0545 | 0.10677 | 0.15223 | 0.50182 | 0.084371 | 0.86074 | 0.3724
2025-06-21 05:00 | 34.7124 | 6.1074 | 0.83943 | 0.83976 | 16.2108 | 4.1851 | 12.6702 | 192.8429 | 16.1669 | 193.5224 | 26.9294 | 23.2502 | 13.8697 | 197.6551 | 32.1002 | 11.5417 | 13.5979 | 195.4247 | 18.2912 | 45.8545 | 13.9348 | 195.6907 | 18.7305 | 45.8728 | 13.8879 | 196.9327 | 194.5443 | 13.119 | 45.3382 | 0.041071 | 9.9692 | 0 | 81.1179 | 21.2752 | 54.5628 | 13.3714 | 190.9525 | 194.3407 | 13.0154 | 3.5555 | 50.3976 | 94.8767 | 145.2742 | 10.8837 | 135.8488 | 96.5141 | 16.7232 | 6.8118 | 83.552 | 14.1843 | 0.82401 | 0.18963 | 1.981 | 94.4576 | 0.10649 | 0.15826 | 0.6038 | 0.084137 | 1.2213 | 0.3715
2025-06-21 06:00 | 35.017 | 5.0357 | 0.79736 | 0.80101 | 15.947 | 4.1173 | 12.786 | 193.2626 | 16.1561 | 193.897 | 26.6438 | 24.025 | 13.9849 | 198.0578 | 32.1042 | 11.7823 | 13.7086 | 195.8134 | 18.1704 | 46.0251 | 14.0306 | 195.9884 | 18.6526 | 46.0378 | 13.9918 | 197.2206 | 194.9572 | 13.2357 | 45.1674 | 0.039249 | 9.9701 | 0 | 81.0032 | 21.2793 | 53.6013 | 13.4805 | 191.3359 | 194.7478 | 13.1275 | 3.5338 | 49.6736 | 94.5009 | 144.1745 | 10.8173 | 135.3623 | 96.3649 | 16.7229 | 6.7693 | 83.2596 | 14.1571 | 0.82196 | 0.1949 | 1.9974 | 93.7569 | 0.10647 | 0.15847 | 0.60416 | 0.084129 | 1.5099 | 0.37262
2025-06-21 07:00 | 34.9812 | 6.0808 | 0.79663 | 0.79724 | 16.8504 | 4.1469 | 12.742 | 193.1305 | 16.295 | 193.9871 | 26.5633 | 24.1818 | 13.9546 | 197.9619 | 32.1091 | 10.8496 | 13.6721 | 195.7476 | 18.1733 | 46.0304 | 13.9782 | 195.9266 | 18.6264 | 46.0451 | 13.9585 | 197.1162 | 194.8354 | 13.1941 | 45.2143 | 0.048271 | 9.9714 | 0 | 80.9899 | 21.3128 | 53.4809 | 13.4497 | 191.339 | 194.6202 | 13.0848 | 3.4532 | 49.3624 | 95.7003 | 145.0627 | 11.0207 | 136.9147 | 96.6801 | 16.7241 | 6.9149 | 82.5787 | 14.2514 | 0.79485 | 0.20082 | 2.0419 | 93.742 | 0.10798 | 0.13802 | 0.56382 | 0.085997 | 1.1747 | 0.37902
2025-06-21 08:00 | 34.4277 | 7.5364 | 0.85331 | 0.87059 | 18.8063 | 4.2385 | 12.6488 | 192.7889 | 16.4866 | 193.8346 | 26.0334 | 23.9925 | 13.8717 | 197.5942 | 32.1303 | 10.3029 | 13.5843 | 195.4454 | 18.2093 | 46.0364 | 13.8741 | 195.6963 | 18.6583 | 46.0611 | 13.8736 | 196.8195 | 194.4747 | 13.0955 | 44.8638 | 0.062998 | 9.9757 | 0 | 81.1106 | 21.3472 | 54.7626 | 13.3752 | 191.1056 | 194.2784 | 12.9922 | 3.4894 | 48.5613 | 97.362 | 145.9233 | 11.5934 | 137.7933 | 96.0901 | 16.1576 | 7.002 | 83.3379 | 14.4309 | 0.75141 | 0.2048 | 2.0542 | 94.6238 | 0.1108 | 0.11614 | 1.2465 | 0.089266 | 0.82238 | 0.38428
2025-06-21 09:00 | 34.6717 | 7.6079 | 0.89119 | 0.92257 | 19.9767 | 4.1954 | 12.6629 | 192.8352 | 16.6299 | 193.7004 | 26.3976 | 25.1968 | 13.9508 | 197.8021 | 32.1469 | 11.25 | 13.6352 | 195.5638 | 18.2297 | 46.0367 | 13.9249 | 195.8023 | 18.6872 | 46.0739 | 13.9139 | 196.9658 | 194.5781 | 13.1317 | 45.8581 | 0.078894 | 9.9782 | 0 | 81.3534 | 21.3617 | 54.8763 | 13.402 | 191.2321 | 194.3272 | 13.0085 | 3.4722 | 52.0341 | 93.4272 | 145.4613 | 12.1382 | 135.7101 | 96.4632 | 15.1828 | 6.8444 | 83.4237 | 14.6283 | 0.70053 | 0.17947 | 2.0003 | 93.9903 | 0.11325 | 0.11133 | 2.2692 | 0.092286 | 0.98576 | 0.37791
2025-06-21 10:00 | 34.7652 | 6.715 | 0.86712 | 0.89097 | 19.8784 | 4.3186 | 12.698 | 192.9487 | 16.8622 | 193.7861 | 26.2191 | 26.1202 | 14.0172 | 197.9683 | 32.1508 | 11.9996 | 13.6808 | 195.701 | 18.2412 | 46.0356 | 13.9783 | 195.9308 | 18.6617 | 46.0727 | 13.9501 | 197.0948 | 194.6883 | 13.1659 | 45.7612 | 0.06895 | 9.9785 | 0 | 81.596 | 21.3545 | 54.6894 | 13.4348 | 191.3925 | 194.4362 | 13.0403 | 3.4628 | 54.5407 | 95.5978 | 150.1385 | 12.5875 | 136.8616 | 96.8063 | 14.9132 | 6.9562 | 83.4133 | 14.7965 | 0.8031 | 0.15809 | 2.064 | 94.3107 | 0.11341 | 0.11104 | 3.8622 | 0.092462 | 1.1791 | 0.36882
2025-06-21 11:00 | 33.8699 | 5.3912 | 0.86395 | 0.89591 | 20.0262 | 4.5654 | 12.6035 | 192.6287 | 16.9494 | 193.7838 | 24.656 | 24.735 | 13.8278 | 197.341 | 32.1554 | 12.0499 | 13.5293 | 195.2494 | 18.2462 | 46.0367 | 13.8371 | 195.5668 | 18.6317 | 46.0747 | 13.806 | 196.6389 | 194.2227 | 13.0226 | 43.5986 | 0.045709 | 9.9809 | 0 | 81.7048 | 21.3369 | 55.0491 | 13.3313 | 191.0863 | 194.0866 | 12.9383 | 3.3125 | 49.1102 | 105.5205 | 154.6307 | 12.417 | 140.68 | 96.6285 | 15.8738 | 7.4364 | 83.4103 | 14.8012 | 0.96691 | 0.17849 | 2.1465 | 94.5631 | 0.11211 | 0.11 | 5.0839 | 0.090476 | 0.91729 | 0.36625
2025-06-21 12:00 | 34.0826 | 4.9451 | 0.91665 | 0.96276 | 20.5841 | 4.8214 | 12.6066 | 192.6387 | 17.0823 | 193.7338 | 24.0994 | 25.3916 | 13.8531 | 197.3943 | 32.4522 | 15.1588 | 13.5878 | 195.3709 | 18.242 | 46.0376 | 13.8711 | 195.6786 | 18.6759 | 46.0752 | 13.8434 | 196.7584 | 194.2131 | 13.0216 | 43.3948 | 0.045687 | 9.9805 | 0 | 81.7663 | 21.3299 | 54.9569 | 13.3324 | 191.0223 | 194.0936 | 12.942 | 3.284 | 46.5047 | 117.8221 | 164.3268 | 12.1099 | 149.0408 | 96.2647 | 19.6949 | 8.5547 | 82.8705 | 14.7138 | 0.98472 | 0.19298 | 2.3669 | 94.37 | 0.1122 | 0.10976 | 5.9685 | 0.090005 | 0.9879 | 0.3678
2025-06-21 13:00 | 35.1127 | 6.2759 | 0.9589 | 1.0061 | 20.6612 | 5.0405 | 12.7768 | 193.1895 | 17.1563 | 194.1888 | 25.1363 | 27.5614 | 14.1546 | 198.35 | 32.3249 | 17.739 | 13.8639 | 196.1442 | 18.1574 | 46.0367 | 14.1032 | 196.3307 | 18.6249 | 46.0745 | 14.0879 | 197.4867 | 194.8823 | 13.2313 | 44.9078 | 0.048236 | 9.9767 | 0 | 81.8179 | 21.3273 | 53.8798 | 13.4973 | 191.4385 | 194.6815 | 13.1145 | 3.5373 | 52.7944 | 124.1906 | 176.985 | 11.925 | 155.08 | 96.8615 | 23.6421 | 9.4989 | 83.6858 | 14.5774 | 0.95545 | 0.17093 | 2.5773 | 95.6211 | 0.11282 | 0.10982 | 4.5109 | 0.090312 | 1.547 | 0.36799
2025-06-21 14:00 | 35.142 | 6.9838 | 0.95274 | 0.99589 | 20.3746 | 4.9822 | 12.7592 | 193.1503 | 16.8254 | 194.2898 | 25.9472 | 28.7109 | 14.1516 | 198.4116 | 31.8278 | 16.6237 | 13.8129 | 195.8987 | 18.3529 | 42.8548 | 14.0226 | 196.0355 | 18.5868 | 44.553 | 14.0147 | 197.3279 | 194.841 | 13.2095 | 44.8413 | 0.045833 | 9.9757 | 0 | 81.8123 | 21.333 | 53.4226 | 13.4768 | 191.4093 | 194.6438 | 13.0962 | 3.5092 | 54.2703 | 120.8139 | 175.0842 | 11.453 | 151.737 | 97.9524 | 24.5909 | 9.4281 | 79.7739 | 14.3491 | 0.96249 | 0.15149 | 2.4748 | 95.2579 | 0.11213 | 0.10983 | 1.3592 | 0.089756 | 1.4334 | 0.36455
2025-06-21 15:00 | 34.8996 | 5.7265 | 0.92675 | 0.96978 | 19.9309 | 4.8464 | 12.5864 | 192.5795 | 16.6395 | 193.854 | 26.1555 | 30.2058 | 14.0025 | 197.9729 | 31.7486 | 17.8669 | 13.623 | 195.2414 | 18.3277 | 39.7404 | 13.8122 | 195.2489 | 18.777 | 43.5406 | 13.8177 | 196.7379 | 194.232 | 13.0215 | 44.5855 | 0.045725 | 9.9752 | 0 | 81.7647 | 21.3275 | 54.9913 | 13.3139 | 190.9465 | 194.0716 | 12.9277 | 3.2756 | 49.1074 | 120.0308 | 169.1382 | 11.2354 | 150.5545 | 96.869 | 24.591 | 9.2446 | 75.0158 | 14.1767 | 0.99569 | 0.1635 | 2.4614 | 94.826 | 0.1111 | 0.11041 | 0.079832 | 0.088926 | 0.89949 | 0.362
2025-06-21 16:00 | 35.3281 | 4.4544 | 0.92635 | 0.96982 | 19.4398 | 4.9328 | 12.6121 | 192.619 | 17.0449 | 193.8255 | 25.9156 | 31.531 | 14.0787 | 198.2174 | 31.613 | 19.7495 | 13.6955 | 195.4435 | 18.7312 | 40.4051 | 13.9102 | 195.514 | 19.0471 | 44.0562 | 13.914 | 197.0365 | 194.2871 | 13.0525 | 44.8165 | 0.042745 | 9.9722 | 0 | 81.6537 | 21.29 | 56.1155 | 13.3337 | 190.9065 | 194.1313 | 12.9553 | 3.3054 | 49.1936 | 125.0731 | 174.2668 | 11.9187 | 154.7454 | 97.1709 | 24.59 | 9.818 | 79.2035 | 14.4298 | 1.0184 | 0.17815 | 2.6136 | 95.271 | 0.10971 | 0.1156 | 5.108 | 0.087765 | 0.91842 | 0.36194
2025-06-21 17:00 | 35.8482 | 4.4788 | 0.9314 | 0.96906 | 18.7335 | 4.9279 | 12.8669 | 193.5224 | 17.2975 | 194.4258 | 26.1819 | 31.8123 | 14.3662 | 199.2064 | 31.3923 | 19.653 | 13.9917 | 196.4172 | 19.55 | 41.0062 | 14.2232 | 196.615 | 19.0616 | 44.0575 | 14.2048 | 198.071 | 195.2522 | 13.3304 | 45.6049 | 0.036559 | 9.9701 | 0 | 81.4806 | 21.2589 | 53.2183 | 13.5631 | 191.5832 | 195.0716 | 13.2067 | 3.9611 | 53.1522 | 123.503 | 176.6552 | 12.2663 | 156.0904 | 97.8523 | 25.1624 | 10.222 | 83.1396 | 14.6379 | 1.0335 | 0.18633 | 2.6581 | 95.3306 | 0.10801 | 0.12838 | 5.5164 | 1.986 | 2.9243 | 0.36385
2025-06-21 18:00 | 35.9889 | 4.5906 | 0.91968 | 0.95412 | 18.1675 | 4.8991 | 13.0321 | 194.1201 | 17.2628 | 194.8261 | 26.7248 | 30.8591 | 14.525 | 199.7718 | 31.1117 | 18.7726 | 14.148 | 197.0242 | 19.2566 | 41.0129 | 14.355 | 197.0164 | 19.0392 | 43.1961 | 14.3373 | 198.56 | 195.854 | 13.4993 | 45.5981 | 0.032968 | 9.9709 | 0 | 81.2996 | 21.2875 | 49.3385 | 13.7133 | 192.0722 | 195.6955 | 13.3679 | 4.4522 | 54.5942 | 121.7205 | 176.3147 | 12.2038 | 156.0579 | 97.4331 | 26.1453 | 10.319 | 82.6508 | 14.5976 | 1.0432 | 0.18783 | 2.6636 | 95.1288 | 0.10719 | 0.13925 | 0.47756 | 1.9863 | 3.5722 | 0.36582
2025-06-21 19:00 | 35.6281 | 3.6729 | 0.91434 | 0.94769 | 18.2243 | 4.6998 | 12.8818 | 193.591 | 16.7887 | 194.745 | 26.9598 | 29.8787 | 14.3682 | 199.3003 | 30.9056 | 17.9911 | 13.9872 | 196.5659 | 18.9888 | 41.014 | 14.1914 | 196.5049 | 19.1703 | 42.2059 | 14.1766 | 197.9988 | 195.3033 | 13.3375 | 45.2554 | 0.03215 | 9.9709 | 0 | 81.1266 | 21.3307 | 50.0036 | 13.5745 | 191.6747 | 195.1558 | 13.2215 | 4.0253 | 54.381 | 113.0641 | 167.4451 | 11.264 | 149.1449 | 97.2224 | 26.5545 | 9.5993 | 81.968 | 14.3453 | 1.05 | 0.18898 | 2.4416 | 94.3354 | 0.82719 | 0.14204 | 0.070003 | 8.455 | 1.8018 | 0.36665
2025-06-21 20:00 | 35.3054 | 3.0866 | 0.91887 | 0.95092 | 18.3633 | 4.3237 | 12.7049 | 192.9779 | 16.3837 | 194.355 | 27.2527 | 28.8775 | 14.2367 | 198.8972 | 30.9103 | 17.9899 | 13.86 | 196.1226 | 19.6506 | 41.1803 | 14.0965 | 196.3023 | 19.4224 | 42.0778 | 14.0658 | 197.5743 | 194.76 | 13.1783 | 46.4786 | 0.038059 | 9.9686 | 0 | 80.9517 | 21.3345 | 51.8833 | 13.4163 | 191.1582 | 194.5387 | 13.056 | 3.5763 | 53.552 | 99.0981 | 152.6501 | 10.3215 | 141.037 | 96.3435 | 24.2295 | 8.428 | 81.5879 | 14.1975 | 1.0531 | 0.19226 | 2.1843 | 94.1988 | 2.4299 | 0.14115 | 0.069989 | 21.8414 | 1.4673 | 0.36674
2025-06-21 21:00 | 35.4423 | 2.8085 | 0.92457 | 0.95452 | 18.6092 | 4.206 | 12.6973 | 192.956 | 16.415 | 194.2014 | 27.5431 | 28.6772 | 14.2535 | 198.946 | 30.9259 | 18.2267 | 13.8787 | 196.1634 | 19.7373 | 41.6435 | 14.1292 | 196.4043 | 19.5165 | 42.079 | 14.0871 | 197.7234 | 194.7973 | 13.1893 | 47.3496 | 0.039461 | 9.9657 | 0 | 80.7883 | 21.2991 | 50.1559 | 13.4113 | 191.114 | 194.522 | 13.0514 | 3.5544 | 53.4995 | 95.5714 | 149.0709 | 10.826 | 139.3463 | 95.973 | 20.4661 | 8.0615 | 81.5273 | 14.2941 | 1.0463 | 0.19466 | 2.1217 | 94.1392 | 1.7104 | 0.13723 | 0.070128 | 25.739 | 1.7516 | 0.36609
2025-06-21 22:00 | 35.3339 | 3.318 | 0.90567 | 0.93949 | 18.5965 | 4.108 | 12.6351 | 192.7507 | 16.1827 | 194.3705 | 27.8356 | 29.6213 | 14.1933 | 198.7601 | 30.9559 | 17.5389 | 13.803 | 195.8842 | 19.3182 | 41.7068 | 14.0525 | 196.1014 | 19.469 | 41.8351 | 14.0099 | 197.518 | 194.5867 | 13.1236 | 47.359 | 0.036888 | 9.9688 | 0 | 80.6335 | 21.2833 | 48.2807 | 13.3493 | 190.9486 | 194.3031 | 12.9889 | 3.3958 | 53.968 | 91.1842 | 145.1521 | 10.7403 | 134.676 | 96.1783 | 18.3913 | 7.5169 | 80.8649 | 14.2164 | 1.043 | 0.18993 | 1.9671 | 93.6568 | 0.87865 | 0.13556 | 0.070138 | 28.0022 | 1.3202 | 0.36351
2025-06-21 23:00 | 34.9187 | 4.3276 | 0.87341 | 0.91537 | 18.3465 | 3.9484 | 12.543 | 192.4293 | 15.9058 | 194.3157 | 27.9937 | 29.9862 | 14.0886 | 198.4362 | 31.1303 | 15.8031 | 13.6845 | 195.4443 | 19.293 | 41.2178 | 13.9384 | 195.6889 | 19.4945 | 41.3189 | 13.8945 | 197.1075 | 194.2437 | 13.0221 | 47.1939 | 0.030734 | 9.9737 | 0 | 80.4643 | 21.2871 | 48.2675 | 13.2613 | 190.65 | 193.9628 | 12.8991 | 3.1874 | 53.536 | 84.3377 | 137.8737 | 10.5582 | 129.1873 | 95.7475 | 16.5034 | 6.6728 | 80.6879 | 14.099 | 1.0508 | 0.18999 | 1.8053 | 93.2868 | 2.1478 | 0.13743 | 0.069798 | 32.0218 | 0.83313 | 0.3608
2025-06-22 | 33.785 | 4.5474 | 0.86656 | 0.89975 | 18.2253 | 3.9897 | 12.5262 | 192.3794 | 15.9277 | 194.0341 | 28.4102 | 29.9889 | 14.079 | 198.398 | 31.2982 | 14.9909 | 13.661 | 195.3701 | 19.2735 | 40.9675 | 13.9179 | 195.5087 | 19.5093 | 41.0526 | 13.8692 | 196.8447 | 194.1876 | 13.0073 | 47.3658 | 0.021185 | 9.9713 | 0 | 80.2772 | 21.2709 | 48.2752 | 13.2465 | 190.593 | 193.9084 | 12.8816 | 3.1162 | 52.548 | 82.2448 | 134.7929 | 11.4468 | 130.3158 | 98.1122 | 14.9264 | 6.4498 | 79.3473 | 14.1798 | 2.4867 | 1.7981 | 1.7476 | 93.5899 | 2.9392 | 0.13799 | 1.4953 | 31.5375 | 2.1719 | 1.722
Total | MW: 837.0881; MVAR: 126.472; kg/s: 3923250.282; kg/s: 304709.2919; kg/s: 4440152.4816; kg/s: 8895178.2147; kg/s: 13335330.6963; kg/s: 12219667.5845
Average | 34.8787 | 5.2697 | 0.87886 | 0.9055 | 18.3913 | 4.4228 | 12.6829 | 192.9024 | 16.5238 | 193.9696 | 26.579 | 26.7962 | 14.0345 | 198.1488 | 31.7467 | 14.534 | 13.7067 | 195.6869 | 18.6581 | 43.6331 | 13.9783 | 195.8781 | 18.8999 | 44.4292 | 13.9506 | 197.1732 | 194.6137 | 13.1369 | 45.408 | 0.0445 | 9.9725 | 0 | 81.2592 | 21.3065 | 52.7933 | 13.3963 | 191.129 | 194.4138 | 13.0268 | 3.5267 | 51.3907 | 102.9535 | 154.3441 | 11.334 | 141.4313 | 96.6288 | 19.5283 | 7.8683 | 81.99 | 14.3552 | 0.9857 | 0.25241 | 2.1673 | 94.3021 | 0.53766 | 0.13196 | 1.6767 | 6.3738 | 1.3783 | 0.42542
Min | 33.785 | 2.8085 | 0.77483 | 0.78996 | 15.947 | 3.9484 | 12.5262 | 192.3794 | 15.9058 | 193.3264 | 24.0994 | 22.0404 | 13.7187 | 197.1764 | 30.9056 | 10.1071 | 13.4532 | 194.9754 | 18.1574 | 39.7404 | 13.7937 | 195.2489 | 18.5868 | 41.0526 | 13.7459 | 196.5318 | 194.0927 | 12.9788 | 43.3948 | 0.021185 | 9.9657 | 0 | 80.2772 | 21.2589 | 48.2675 | 13.2465 | 190.593 | 193.9084 | 12.8816 | 3.1162 | 46.5047 | 82.2448 | 134.7929 | 10.3215 | 129.1873 | 95.5414 | 14.9132 | 6.4498 | 75.0158 | 14.0735 | 0.70053 | 0.15149 | 1.7476 | 93.2868 | 0.10647 | 0.10976 | 0.068706 | 0.084129 | 0.82238 | 0.3608
Max | 35.9889 | 7.6079 | 0.9589 | 1.0061 | 20.6612 | 5.0405 | 13.0321 | 194.1201 | 17.2975 | 194.8261 | 28.4102 | 31.8123 | 14.525 | 199.7718 | 32.4522 | 19.7495 | 14.148 | 197.0242 | 19.7373 | 46.0376 | 14.355 | 197.0164 | 19.5165 | 46.0752 | 14.3373 | 198.56 | 195.854 | 13.4993 | 47.3658 | 0.078894 | 9.9809 | 0 | 81.8179 | 21.3617 | 56.1155 | 13.7133 | 192.0722 | 195.6955 | 13.3679 | 4.4522 | 54.5942 | 125.0731 | 176.985 | 12.5875 | 156.0904 | 98.1122 | 26.5545 | 10.319 | 83.6858 | 14.8012 | 2.4867 | 1.7981 | 2.6636 | 95.6211 | 2.9392 | 0.15847 | 5.9685 | 32.0218 | 3.5722 | 1.722

## pH Monitoring
No | pH Value (Brine Condensate Line)
| Tanggal | (Shift) | Jam | pH value | Temp. (⁰C)
1 | 2025-06-01 | Day | 14:30 | 5.06 | 33.6
2 |  | Night | 7:00 | 5.16 | 27.7
3 | 2025-06-02 | Day | 16:19 | 5.16 | 33.9
4 |  | Night | 6:30 | 4.8 | 30.8
5 | 2025-06-03 | Day | 17:35 | 5.03 | 30.6
6 |  | Night | 7:00 | 4.89 | 30.8
7 | 2025-06-04 | Day | 16:39 | 5.59 | 26.4
8 |  | Night | 1:42 | 5.27 | 29.6
9 | 2025-06-05 | Day | 14:00 | 5.17 | 27.5
10 |  | Night | 1:12 | 5.27 | 27
11 | 2025-06-06 | Day | 16:55 | 6.66 | 28.1
12 |  | Night | 1:10 | 5.09 | 30.4
13 | 2025-06-07 | Day | 15:18 | 5.12 | 25.1
14 |  | Night | 1:20 | 5.18 | 33.4
15 | 2025-06-08 | Day | 15:10 | 5.31 | 23.9
16 |  | Night | 0:50 | 5.33 | 34.4
17 | 2025-06-09 | Day | 19:30 | 5.27 | 31.1
18 |  | Night | 22:15 | 5.55 | 22.2
19 | 2025-06-10 | Day | 8:55 | 5.69 | 31.6
20 |  | Night | 0:20 | 5.18 | 24.3
21 | 2025-06-11 | Day | 17:00 | 5.07 | 21.6
22 |  | Night | 22:30 | 5.62 | 28.8
23 | 2025-06-12 | Day | 10:10 | 5.08 | 27.3
24 |  | Night | 21:30 | 5.64 | 26.6
25 | 2025-06-13 | Day | 8:40 | 5.11 | 27.1
26 |  | Night | 22:00 | 5.77 | 25.5
27 | 2025-06-14 | Day | 10:00 | 5.55 | 32
28 |  | Night | 22:00 | 5.78 | 28.9
29 | 2025-06-15 | Day | 10:00 | 5.33 | 24.6
30 |  | Night | 23:45 | 5.82 | 30.3
31 | 2025-06-16 | Day | 9:40 | 5.44 | 27.9
32 |  | Night | 23:45 | 5.97 | 23.8
33 | 2025-06-17 | Day | 15:30 | 5.77 | 33
34 |  | Night | 22:45 | 5.86 | 27.7
35 | 2025-06-18 | Day | 10:35 | 5 | 21
36 |  | Night | 23:30 | 5.97 | 21.6
37 | 2025-06-19 | Day | 18:05 | 5.47 | 21.3
38 |  | Night | 23:45 | 5.41 | 31.3
39 | 2025-06-20 | Day | 17:56 | 5.5 | 26.5
40 |  | Night | 0:00 | 5.34 | 27.9
41 | 2025-06-21 | Day | 17:20 | 5.66 | 31.2
42 |  | Night | 0:00 | 5.3 | 27.7
43 | 2025-06-22 | Day
44 |  | Night
45 | 2025-06-23 | Day
46 |  | Night
47 | 2025-06-24 | Day
48 |  | Night
49 | 2025-06-25 | Day
50 |  | Night
51 | 2025-06-26 | Day
52 |  | Night
53 | 2025-06-27 | Day
54 |  | Night
55 | 2025-06-28 | Day
56 |  | Night
57 | 2025-06-29 | Day
58 |  | Night
59 | 2025-06-30 | Day
60 |  | Night

## Running Hours (hidden)
DATE: | 2025-06-21
I.) IJN 6
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Electrical Pit Pump |  |  |  |  | 0 | 0
Diesel Pit Pump |  |  |  |  | 0 | 0
II.) IJN 8
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Booster Pump A | Booster Pump A |  |  |  | 0 | 0
Booster Pump B | Booster Pump B |  |  |  | 0 | 0
Pit Pump |  |  |  |  | 0 | 0
III.) POWER BLOCK
Equipment |  | LAST DAY OF | PREVIOUS | PRESENT | DAY | MTD
|  | PREVIOUS MONTH | DAY | DAY | DIFFERENCE | DIFFERENCE
Reinjection Pump A |  |  |  |  | 0 | 0
Reinjection Pump B |  |  |  |  | 0 | 0
Condensate Pump A |  |  |  |  | 0 | 0
Condensate Pump B |  |  |  |  | 0 | 0
Feed Pump A |  |  |  |  | 0 | 0
Feed Pump B |  |  |  |  | 0 | 0
Feed Pump C |  |  |  |  | 0 | 0
Fire Water Refiling Pump |  |  |  |  | 0 | 0
Oil Sump Pit Pump |  |  |  |  | 0 | 0
Compressor A |  |  |  |  | 0 | 0
Compressor B |  |  |  |  | 0 | 0